Addendum to Operations and Maintenance Plan Annual Reporting 2009 – Iqaluit LTU License # 1BR-LTU1013

Part E Section 3

a)

a. Table of Contents

b. Effective date of Plan

c. Inspection and maintenance procedures

d. Procedure for snow removal/treatment

e. Dust control

f. Access to site

g. Soil characterization in LTU

h. Maintenance procedures

i. Maintenance frequency

j. Monitoring well operations

k. PCBs on site

l. QA/QC plan

m. Environment Canada recommandations 

b) Effective date: January 1, 2010

c) Franz Environmental was hired to inspect the LTU facility to complete “As Built Drawing” and inspect the LTU and monitoring wells to ensure the LTU is functioning properly in September 2009 (attached report is located in the “As Built Drawings.”  The LTU facility will be inspected once per year to ensure it is performing as it is designed.  The following parameters are used to assess the LTU facility:

i. Cell Dike Crest – the height of the dike ensuring the proper slope is maintained

ii. Liner Anchor – the material used to anchor the liner to ensure it is properly seated on the berm.  This also requires a certain slope for stability and ensures the liner is locked into place.

iii. Base – the base of the LTU is assessed to endure it is on a “prepared surface” to ensure a flat smooth surface to construct the LTU on.

iv. Drainage – the LTU is constructed with a designated slope for water to drain to one side in the sump area.

v. Contaminated Soil – is assessed to ensure what contaminants are placed in the LTU and placed to a certain depth, usually 1 meter.

vi. Monitoring Wells – are assessed for location and functionality.  

Franz Environmental reviewed the above aspects for both LTU cells and concluded the cells are in acceptable with recommendations.  The recommendations are as follows:

1) Some soil is located in the sump area of LTU cell C that should be removed.

2) Additional fill material should be added to the NE and SE berms of the LTU Cell D 

3) Soil berms in Cell D should be reinforced with additional fill material to achieve a 50% grade.

4) Larger items (concrete and asphalt) should be removed. 

d) No snow removal is required at the LTU facility.

e) Dust has not been an issue at the LTU.  Precipitation infiltration has not been an issue at the facility due to the low volumes of precipitation recorded at this location.  If the sump of the LTU becomes full, the water can be treated first prior to removal or removed and sent to a facility to treat the water.  To date, no discharge has been required.

f) The location of the LTU is on the restricted airport property.  No access to the site is allowed.

g) The soil deposited into the facility is tested and verified at a certified lab for the contents.  No PCBs are lowed in the facility.  Only soil contaminated with petroleum hydrocarbons will be accepted into the LTU.

h)
Nutrient Amendments and Tilling 

Biodegradation requires micro-organisms are meeting nutritional requirements.  The optimal range of carbon:nitrogen:phosphorus (C:N:P) is 100:10:1 to 100:1:0.5.  Soil amendments in the form of commercially used solid fertilizers will be applied in sufficient amounts as recommended by the manufacturer to achieve this target ratio for the specified volume of soil in the LTU.

Once the nutrients have been added to the LTU the soil will be turned over with the use of a backhoe.  This will expose the soil to oxygen and for micro-organisms as well as distributes nutrients and moisture in the soil, thereby aiding in biodegradation.  Care must be taken by the backhoe operator not to tear the liner and report any cracks, blisters or punctures to the liner.
Leachate Management 

The LTU is constructed with a 1% slope which allows any leachate to collect in the sump area.  Visual monitoring of the sump ensures that water is collecting in the sump area indicates the liner is not damaged.  Leachate may be recirculated over the LTU soil surface as a means of irrigation to maintain optimal biodegradation rates.  Discharge of the leachate may be required if the sump collection area rises to within 1 foot of the top of the berm.  This is not likely to happen due to the height of the engineered berms taking into consideration the amount of precipitation and evaporation rates at this location.  If the leachate is required to be discharged it must first meet the discharge levels within CCME EQGs and the Water License 1BR-LTU0608 agreement for LTU wastewater discharge criteria:

	Parameter
	Maximum Allowable Concentration

(ug/l)

	Oil & Grease
	5000

	Lead
	1

	Benzyene
	370

	Toluene
	2

	Ethylbenzene
	90


The area designated for leachate disposal is located adjacent to the LTU in the open field between Apron I and the runway.  This area is located greater then 1 km away from any water body and potable water source.

The LTU will continue to be monitored each field season to ensure the facility is operating as it has been designed.  Additional soil sampling will be conducted in the fall of each year to determine the effectiveness of the previous amendments in the spring.  A soil sampling program will be conducted in August or September as described earlier including monitoring wells.  The following outlines when the samples and activities will be conducted:

	Activity
	Time of Year
	Time of Year

	Soil Sample
	June
	August - September

	Monitoring Well Sample
	June
	August - September

	Tilling/Fertilizer
	June
	If Required Aug - Sept


    i)
Monitoring Well Sampling

TC will undertake sampling the monitoring wells and the sump inside the LTU as described in the Water License No. 1BR-LTU0608.  The frequency and time of year are outlined in the above table.  The sump will be tested prior to any required discharge and tested prior to the decommissioning of the facility.  The parameters for testing the monitoring wells are as follows:

	Station 
	Location
	Parameter 
	Frequency

	LTU -1
	Sump
	PTH, BTEX, HM,PAH
	Discharge

	LTU – MW1
	Upgradient - LTU
	PTH, BTEX, HM,PAH
	Twice/year

	LTU – MW2
	Downgradient - LTU
	PTH, BTEX, HM,PAH
	Twice/year

	LTU – MW3
	Downgradient - LTU
	PTH, BTEX, HM,PAH
	Twice/year


j) Franz Environmental was contracted in September 2009 to inspect the LTU facility and monitoring wells.  All wells are working properly and the LTU cells are also working as designed.  Please as the “As Built Drawings” for the report and more details included.

k) No PCBs present in facility.  PCB contaminated soil is not allowed in the LTU.

l) All samples must be sent to an accredited lab according to ISO/IEC Standard 17025.  The contractor taking the samples must adhere to the CCME Guidance Manual on Sampling, Analysis, and Data Management for Contaminated Sites, 1993.  The QA/QC Sampling program is as follows:

Sampling Program

The first objective is to conduct a comprehensive soil sampling program at the beginning of each field season to identify the levels of PHC contamination in the soil.  Due to the long winter season at this location, TC anticipates initially sampling the LTU in the beginning of June depending on weather conditions.  The soil criteria used for this site will be under the CCME Canada Wide Standards for Petroleum Hydrocarbon Contaminated Soils Tier 1, coarse grain soil, Industrial site.  This criteria is used due to the location of the facility between Runway 18-35 and Apron I.  To access the site airport security clearance is required.  The location will not be used for commercial development due to the location adjacent to the runway and Apron.
1a)  The sampling program will require eight (8) composite soil samples and a sample from each monitoring well from the LTU for submission to a laboratory for analysis. The sampling protocol for the LTU will require a random grid pattern covering the entire area. All sampling procedures will be in accordance with the standards contained in the CCME Guidance Manual on Sampling, Analysis and Data Management for Contaminated Sites Volume I &II. Quality assurance/quality control will be observed while conducting the sampling program and include at a minimum the following:

· Use of trip, field and equipment blanks; 

· Use of duplicate and spiked samples;

· Proper sample containment, preservation, chain of custody; and 

· Due regard for necessary health and safety precautions. 

1b)  All samples should be analyzed for the following parameters: 

· BTEX;

· Total Extractable Hydrocarbons (TEH); 

· CCME Canada Wide Standards for Petroleum Hydrocarbons in Soil for Fractions #1 to #4 for the Tier 1 criteria, coarse grain soil for Industrial Sites.

· Polycyclic Aromatic Hydrocarbons (PAH);

· Total Heavy Metals (Al, As, Cd, Co, Cu, Fe, Pb, Mo, Ni, Se, Ag, T1, Zn).

Summary of Tier 1 Levels (mg/kg) for surface soil CCME.*

	Land Use
	Soil Texture
	F 1
	F 2
	F 3
	F 4

	Agriculture
	Coarse grain soil

Fine grain soil
	30b

210 (170a)
	150

150
	300

1300
	2800

5600

	Residential/Parkland
	Coarse grain soil

Fine grain soil
	30b

210(170a)
	150

150
	300

1300
	2800

5600

	Commercial
	Coarse grain soil

Fine grain soil
	320(240a)

320(170a)
	260

260(230a)
	1700

2500
	3300

6600

	Industrial
	Coarse grain soil

Fine grain soil
	320 (240a)

320 (170a)
	260

260 (230a)
	1700

2500
	3300

6600


* Additional Tier 1 levels are presented in Technical Supplement.

a= Where applicable, for protection of potable groundwater.

b= assumes contamination near residence
2a)  The use of a gas Photo Ionization Detector (PID) or similar equipment to monitor hydrocarbon vapours will be required to field screen the soil sample taken.  The use of field screening the soil will provide an immediate representation of the conditions and levels of the PHC in the soil.  This process does not replace laboratory results, however it does give a good sense of the conditions.  

The results of the laboratory analysis are to be compared to the Nunavut Environmental Guidelines for Site Remediation (most current edition), CCME Canada Wide Standards Petroleum Hydrocarbon Guidelines (most current edition) and the CCME Interim Canadian Environmental Quality Criteria for Contaminated Sites (most current edition) remediation criteria for industrial zoned sites.   The selected laboratory must provide quality assurance (QA) and quality control (QC) procedures. All samples are to be procured through approved methods and procedures and are to be submitted to a Certified Laboratory (CAEAL/ Standards Council of Canada) for formal analysis.

m) Environment Canada Information Requests

Comments from Environment Canada letter dated May 7, 2009 from Stacy Lambert (attached) address the following:

1) Additional reinforcement at the toe of the LTU consisted of placing the liner material (60 mil HDPE) on the prepared surface with an additional non-woven polypropylene geotextile (150 EX) liner on top of the HDPE.  The line anchor was also increased in size to ensure the additional weight of precipitation would not lift the liner material from the berm.  The attached Franz investigation report (June 4, 2010) indicates the facility is functioning properly.

2) The attached Franz investigation report (June 4, 2010) indicates the monitoring wells are functioning properly.

3) No PCB contaminated soil is accepted at the LTU.  TC ensures all soil is sampled and sent to an accredited lab for analysis prior to placement into the LTU facility.

4) Sampling protocol and monitoring plans are located in the O&M portion of this submission.

5) No water was encountered in the excavation inside the First Air Cargo Building.    

6) A spill contingency plan has been completed and was submitted to the NIRB in 2008.  It is again included in this submission.

7) EC recommended native grasses for reseeding the location once the facility is decommissioned.  TC would like to request a list of native species of grasses and a list of seed contractors who may supply such seed.  TC supports the use of native vegetation where available.

8)  EC provided further recommendations which have been incorporated in the attached documentation, specifically:

· TC inspects the LTU annually for operation and maintenance purposes;

· Address snow in the LTU;

· Address dust issues;

· Restricted access to the site;

· All soil placed in the LTU is characterized by sampling and analyzed at an accredited lab;

· Provided operations and procedures for O&M., tilling/amendment practices

· TC requires a health and safety plan on site while contractors are working at the location.

9) The soil criteria used under the CCME Guidelines for Industrial Site is appropriate for this location.  The soil is located in a restricted developed infield area of the Iqaluit airport between the runway and Apron I.  The soil is not intended to leave the site making the location logistically unreasonable to use this material as fill at a future date.  

10) TC and the Iqaluit Airport maintain records that are required to be submitted to the NIRB, this is comprise of:

· Description of the size and location of the LTU;

· Quantitative and qualitative data on the soil treated at the site;

· Monitoring data;

· Final destination of the treated soil and its intended use.

11) Mandatory requirements under the Fisheries Act.  TC meets the requirements set forth.

12) CEPA Spill Prevention, no storage of PHC on site.  Emergency line – 24-hour Spill (867) 920-8130.

13) No storage of PHC on site and no re-fueling on site.  Spill containment is required for refuelling practices.

14) Spill response equipment is on site at all times and is mandatory for contractors to have a spill response plan.

15) CEPA – Hazardous Waste: all hazardous waste will be addressed if encountered.  It is not anticipated hazardous waste will be encountered at this location.

16) No hazardous waste on site.

17) Wildlife – no contaminated soil is deposited in a way or area such that it is harmful to migratory birds or waters frequented by migratory birds.

