File No: NWB2CON9901

August 8, 2000

Dave Willis








Land Administrator

Unit 123 – 930 West 1st street

North Vancouver BC V7P 3N4

Re: Spill Contingency Plan  - Part 5, Item 1
Dear Mr. Willis:

The Nunavut Water Board has reviewed the document titled “Spill Contingency Plan for NWT and Nunavut” received March 17, 2000 submitted as required under Part 5, Item 1 of your current water licence.  Conditional approval of the plan is given provided that the following recommended improvements are made:  

i. Preventive Measures section, p.1: According to the water license (Part 5, Item 3), all fuel caches should be 30 m away from the high water mark.

ii. Clean-Up section, p.3: In this section, employee safety should be addressed. The initial action should instruct the employee to first assess and if possible control any danger to human health. Only then, if it is safe to do so, the employee should try to stop or limit the extent of the spill.

iii. Reporting Section, p.4: This section should include the requirement to provide the Inspector with a detailed report of each occurrence (as stated in Part 5, Item 2 (b) of the water licence). The Inspector can be contacted at the Nunavut District Office in Iqaluit, by telephone: 867-975-4298 or fax: 867-979-6445.

General Comments: 

a) It should be clearly stated that spill kits are required at camp locations and all fuel caches greater than 4000 l. As well, the plan should include the water license requirement to have one extra fuel storage container equal to, or greater than, the size of the largest fuel container.

b) It would be useful to include site specific drawings of the facilities and camps in question. This would aid in the identification of potential sources of spills and predicting where spills could migrate. 

The revised plan should be submitted as soon as possible. Should you require clarification or additional information please do not hesitate to contact me at 867-360-6338 or by fax at 867-360-6369.

Sincerely, 

Roger LeBlanc

Technical Advisor 

cc: 
Roxanne Beavers, DIAND

