## SNP Stations
Station | Description | Status
BOS-1a | Raw water supply intake at Aimaokatalok (Spyder) Lake | Inactive
BOS-1b | Raw water supply intake at Stickleback Lake | Inactive; facility not constructed
BOS-2 | Containment Pond discharge | Seasonally active. No discharge
BOS-3 | Sewage Treatment Facility treated effluent discharge | Inactive
BOS-4 | Treated sewage effluent at point prior to entry into Aimaokatalok (Spyder) Lake | Inactive; facility decommissioned
BOS-5 | Effluent from the Bulk Fuel Storage Facility prior to discharge to the tundra | Seasonally active. No discharge
BOS-6 | Effluent from the Landfarm Treatment Facility prior to discharge to the tundra | Inactive; facility decommissioned
BOS-7 | Runoff from the temporary storage area of hydrocarbon contaminated soils prior to discharge to the tundra | Inactive: facility decommissioned
BOS-8 | Seepage/runoff from the ore stockpiles and camp pad, monitored on the tundra to the east of the ore stockpiles | Seasonally active
BOS-9 | Portal Decline, surface water runoff discharged onto the tundra, west of portal | Seasonally active
BOS-10 | Underground Mine Water Sumps, mine water pumped from the underground | Inactive; no underground mining activities

## BOS2
Sample ID |  | BOS2 | BOS2 | BOS2 | BOS2 | Part D Item 6
ALS ID |  | YL2300554-001 | YL2300554-002 | EO2305559-001 | EO2305562-001 | Maximum Average Concentration | Maximum Concentration in Any Grab Sample
Date Sampled |  | 2023-06-05 10:40 | 2023-06-05 10:40 | 2023-06-21 14:00 | 2023-06-25 09:30
Parameter | Units | Water | Water | Water | Water
Conductivity | uS/cm | 954 | 961 | 1210 | 1340
Hardness (as CaCO3) | mg/L | 183 | 187 | 130 | 185
pH | pH | 8.41 | 8.4 | 7.11 | 7.38 | 6.5-9.0
Total Suspended Solids | mg/L | 30.8 | 33.6 | 144 | 141 | 15 | 30
Alkalinity, Total (as CaCO3) | mg/L | 219 | 217 | 46.8 | 18.2
Chloride (Cl) | mg/L | 74.8 | 75.2 | 99.8 | 106
Nitrate (as N) | mg/L | <0.0250 | <0.0250 | 0.0276 | 0.0111 | 130 | 260
Nitrite (as N) | mg/L | <0.0050 | <0.0050 | 0.0052 | <0.0010
Sulfate (SO4) | mg/L | 122 | 123 | 334 | 426
Aluminum (Al)-Total | mg/L | 0.0333 | 0.0347 | 3.06 | 0.377
Antimony (Sb)-Total | mg/L | 0.00153 | 0.00154 | 0.00022 | 0.0003
Arsenic (As)-Total | mg/L | 0.206 | 0.21 | 0.0155 | 0.0282 | 0.05 | 0.1
Barium (Ba)-Total | mg/L | 0.00352 | 0.00366 | 0.00263 | 0.00198
Beryllium (Be)-Total | mg/L | <0.000100 | <0.000100 | <0.000100 | <0.000100
Boron (B)-Total | mg/L | 0.1 | 0.104 | 0.062 | 0.052
Cadmium (Cd)-Total | mg/L | 8.7e-06 | 9.8e-06 | 1.82e-05 | 3.59e-05
Calcium (Ca)-Total | mg/L | 31.6 | 32.6 | 39.3 | 49
Chromium (Cr)-Total | mg/L | 0.00053 | 0.0006 | <0.00050 | 0.00058
Cobalt (Co)-Total | mg/L | 0.0127 | 0.0131 | 0.00602 | 0.00755
Copper (Cu)-Total | mg/L | 0.0135 | 0.014 | 0.00789 | 0.0112 | 0.02 | 0.04
Iron (Fe)-Total | mg/L | 0.663 | 0.699 | 1.67 | 0.898
Lead (Pb)-Total | mg/L | 0.000825 | 0.000852 | 0.000748 | 0.000743 | 0.01 | 0.02
Lithium (Li)-Total | mg/L | 0.0048 | 0.0049 | 0.0019 | 0.002
Magnesium (Mg)-Total | mg/L | 25.3 | 25.6 | 7.68 | 15.2
Manganese (Mn)-Total | mg/L | 0.0982 | 0.1 | 0.0791 | 0.0903
Mercury (Hg)-Total | mg/L | <0.0000050 | <0.0000050 | <0.0000050 | <0.0000050
Molybdenum (Mo)-Total | mg/L | 0.00196 | 0.00195 | 0.000192 | 0.000568
Nickel (Ni)-Total | mg/L | 0.0572 | 0.0585 | 0.0274 | 0.0356 | 0.25 | 0.5
Potassium (K)-Total | mg/L | 23.5 | 23.8 | 44.8 | 24.4
Selenium (Se)-Total | mg/L | 0.000337 | 0.000285 | 0.000204 | 0.000234
Silver (Ag)-Total | mg/L | <0.000010 | <0.000010 | <0.000010 | <0.000010
Sodium (Na)-Total | mg/L | 43.8 | 45.2 | 157 | 175
Strontium (Sr)-Total | mg/L | 0.0984 | 0.0959 | 0.15 | 0.16
Thallium (Tl)-Total | mg/L | <0.000010 | <0.000010 | 3.5e-05 | 0.000116
Tin (Sn)-Total | mg/L | 0.00112 | 0.00116 | 0.00037 | 0.00044
Titanium (Ti)-Total | mg/L | <0.00060 | <0.00090 | 0.00283 | 0.00148
Uranium (U)-Total | mg/L | 0.00022 | 0.000223 | 0.000155 | 0.000172
Vanadium (V)-Total | mg/L | 0.00121 | 0.00124 | 0.00253 | 0.00056
Zinc (Zn)-Total | mg/L | 0.0123 | 0.0127 | 0.0111 | 0.0189 | 0.3 | 0.6
Oil and Grease | mg/L | <5.0 | <5.0 | <5.0 | <5.0 | 5 | 10
Oil And Grease (Visible Sheen) |  | Absent | Absent | Absent | Absent | No visible sheen | No visible sheen
Phenols (4AAP) | mg/L | 0.0094 | 0.0098 | 0.0019 | 0.0053
Benzene | mg/L | <0.00050 | <0.00050 | <0.00050 | <0.00050
Ethylbenzene | mg/L | <0.00050 | <0.00050 | <0.00050 | <0.00050
Methyl t-butyl ether (MTBE) | mg/L | <0.00050 | <0.00050 | <0.00050 | <0.00050
Styrene | mg/L | <0.00050 | <0.00050 | <0.00050 | <0.00050
Toluene | mg/L | <0.00050 | <0.00050 | <0.00050 | <0.00050
Xylenes | mg/L | <0.00075 | <0.00075 | <0.00075 | <0.00075
Acenaphthene | mg/L | <0.000010 | <0.000010 | <0.000010 | <0.000010
Acenaphthylene | mg/L | <0.000010 | <0.000010 | <0.000010 | <0.000010
Acridine | mg/L | <0.000010 | <0.000010 | <0.000010 | <0.000010
Anthracene | mg/L | <0.000010 | <0.000010 | <0.000010 | <0.000010
Benz(a)anthracene | mg/L | <0.000010 | <0.000010 | <0.000010 | <0.000010
Benzo(a)pyrene | mg/L | <0.0000050 | <0.0000050 | <0.0000050 | <0.0000050
Benzo(b+j+k)fluoranthene | mg/L | <0.000015 | <0.000015 | <0.000015 | <0.000015
Benzo(g,h,i)perylene | mg/L | <0.000010 | <0.000010 | <0.000010 | <0.000010
Benzo(k)fluoranthene | mg/L | <0.000010 | <0.000010 | <0.000010 | <0.000010
Chrysene | mg/L | <0.000010 | <0.000010 | <0.000010 | <0.000010
Dibenz(a,h)anthracene | mg/L | <0.0000050 | <0.0000050 | <0.0000050 | <0.0000050
Fluoranthene | mg/L | <0.000010 | <0.000010 | <0.000010 | <0.000010
Fluorene | mg/L | <0.000010 | <0.000010 | <0.000010 | <0.000010
Indeno(1,2,3-c,d)pyrene | mg/L | <0.000010 | <0.000010 | <0.000010 | <0.000010
Naphthalene | mg/L | <0.000050 | <0.000050 | <0.000050 | <0.000050
Phenanthrene | mg/L | <0.000020 | <0.000020 | <0.000020 | <0.000020
Pyrene | mg/L | <0.000010 | <0.000010 | <0.000010 | <0.000010
Quinoline | mg/L | 9.5e-05 | 0.000102 | <0.000092 | <0.000110
Biological Oxygen Demand (BOD5) | mg/L | 22 | 23 | 10.4 | 13.7 | 80 mg/L | 80 mg/L
Fecal Coliforms | CFU/100ml | <1.0 | <1.0 | <1.0 | <1.0 | 10,000 CFU/100ml | 10,000 CFU/100ml
Bold indicates exceedance of Part D Item 6 Maximum Concentration
^ Indicates duplicate sample.

## BOS5
Sample ID |  | BOS5 | BOS5^ | Part D Item 19
ALS ID |  | YL2300561-001 | YL2300561-002 | Maximum Concentration in Any Grab Sample
Date Sampled |  | 2023-06-05 10:15 | 2023-06-05 10:15
Parameter | Units | Water | Water
Conductivity | uS/cm | 846 | 843
Hardness (as CaCO3) | mg/L | 450 | 449
pH | pH Units | 7.92 | 7.9 | 6.5-9.0
Total Suspended Solids | mg/L | 6.8 | 5 | 15
Alkalinity, Total (as CaCO3) | mg/L | 54 | 53.7
Nitrate (as N) | mg/L | <0.0250 | <0.0250
Nitrite (as N) | mg/L | <0.0050 | <0.0050
Chloride (Cl) | mg/L | 7.14 | 6.94
Sulfate (SO4) | mg/L | 402 | 394
Aluminum (Al)-Total | mg/L | 0.0262 | 0.0288
Antimony (Sb)-Total | mg/L | 0.00293 | 0.00295
Arsenic (As)-Total | mg/L | 0.135 | 0.137 | 0.05
Barium (Ba)-Total | mg/L | 0.00553 | 0.00579
Beryllium (Be)-Total | mg/L | <0.000100 | <0.000100
Boron (B)-Total | mg/L | <0.000050 | <0.000050
Cadmium (Cd)-Total | mg/L | 0.105 | 0.103
Calcium (Ca)-Total | mg/L | 0.00014 | 0.000137
Chromium (Cr)-Total | mg/L | 110 | 107
Cobalt (Co)-Total | mg/L | 0.00682 | 0.00698
Copper (Cu)-Total | mg/L | 0.00558 | 0.00568 | 0.04
Iron (Fe)-Total | mg/L | 0.661 | 0.65
Lead (Pb)-Total | mg/L | 0.00853 | 0.00836 | 0.01
Lithium (Li)-Total | mg/L | 0.0068 | 0.0066
Magnesium (Mg)-Total | mg/L | 42.6 | 44.2
Manganese (Mn)-Total | mg/L | 0.0147 | 0.015
Mercury (Hg)-Total | mg/L | <0.0000050 | <0.0000050
Molybdenum (Mo)-Total | mg/L | 0.00139 | 0.00136
Nickel (Ni)-Total | mg/L | 0.0996 | 0.101 | 0.5
Potassium (K)-Total | mg/L | 4.33 | 4.39
Selenium (Se)-Total | mg/L | 0.000263 | 0.000218
Silver (Ag)-Total | mg/L | 1.3e-05 | 1.4e-05
Sodium (Na)-Total | mg/L | 4.84 | 4.94
Strontium (Sr)-Total | mg/L | 0.233 | 0.237
Thallium (Tl)-Total | mg/L | <0.000010 | <0.000010
Tin (Sn)-Total | mg/L | <0.00010 | <0.00010
Titanium (Ti)-Total | mg/L | <0.00030 | <0.00030
Uranium (U)-Total | mg/L | 5.4e-05 | 5.3e-05
Vanadium (V)-Total | mg/L | <0.00050 | <0.00050
Zinc (Zn)-Total | mg/L | 0.0072 | 0.0072 | 0.6
Oil and Grease | mg/L | <5.0 | <5.0 | 15
Oil And Grease (Visible Sheen) |  | Absent | Absent | No visible sheen
Benzene | mg/L | <0.00050 | <0.00050 | 0.37
Ethylbenzene | mg/L | <0.00050 | <0.00050 | 0.91
Methyl t-butyl ether (MTBE) | mg/L | <0.00050 | <0.00050
Styrene | mg/L | <0.00050 | <0.00050
Toluene | mg/L | <0.00050 | <0.00050 | 0.002
Xylenes, Total | mg/L | <0.00075 | <0.00075
Acenaphthene | mg/L | <0.000010 | <0.000010
Acenaphthylene | mg/L | <0.000010 | <0.000010
Acridine | mg/L | <0.000010 | <0.000010
Anthracene | mg/L | <0.000010 | <0.000010
Benz(a)anthracene | mg/L | <0.000010 | <0.000010
Benzo(a)pyrene | mg/L | <0.0000050 | <0.0000050
Benzo(b+j+k)fluoranthene | mg/L | <0.000015 | <0.000015
Benzo(g,h,i)perylene | mg/L | <0.000010 | <0.000010
Benzo(k)fluoranthene | mg/L | <0.000010 | <0.000010
Chrysene | mg/L | <0.000010 | <0.000010
Dibenz(a,h)anthracene | mg/L | <0.0000050 | <0.0000050
Fluoranthene | mg/L | <0.000010 | <0.000010
Fluorene | mg/L | <0.000010 | <0.000010
Indeno(1,2,3-c,d)pyrene | mg/L | <0.000010 | <0.000010
Naphthalene | mg/L | <0.000050 | <0.000050
Phenanthrene | mg/L | <0.000020 | <0.000020
Pyrene | mg/L | <0.000010 | <0.000010
Quinoline | mg/L | <0.000081 | <0.000074
Bold indicates exceedance of Part D Item 19 Maximum Concentration
^ Indicates duplicate sample.

## BOS8
Sample ID |  | BOS8 | BOS8^ | BOS8A | BOS8A^
ALS ID |  | YL2300567-001 | YL2300567-002 | YL2300567-003 | YL2300567-004
Date Sampled |  | 2023-06-05 11:45 | 2023-06-05 11:45 | 2023-06-05 11:20 | 2023-06-05 11:20
Parameter | Units | Water | Water | Water | Water
Conductivity | uS/cm | 641 | 643 | 794 | 788
Hardness (as CaCO3) | mg/L | 303 | 305 | 370 | 378
pH | pH | 8.12 | 8.13 | 8.05 | 8.09
Total Suspended Solids | mg/L | 7.6 | 5.8 | 49 | 21.8
Ammonia, Total (as N) | mg/L | 0.0174 | 0.0115 | 0.0075 | 0.0086
Sulfate (SO4) | mg/L | 205 | 202 | 266 | 262
Aluminum (Al)-Total | mg/L | 0.0141 | 0.012 | 0.181 | 0.176
Antimony (Sb)-Total | mg/L | 0.00302 | 0.00303 | 0.00191 | 0.00194
Arsenic (As)-Total | mg/L | 0.0323 | 0.0323 | 0.0297 | 0.0574
Barium (Ba)-Total | mg/L | 0.00741 | 0.0076 | 0.0107 | 0.0109
Beryllium (Be)-Total | mg/L | <0.000100 | <0.000100 | <0.000100 | <0.000100
Boron (B)-Total | mg/L | 0.058 | 0.055 | 0.084 | 0.084
Cadmium (Cd)-Total | mg/L | 1.44e-05 | 1.33e-05 | 1.13e-05 | 2e-05
Calcium (Ca)-Total | mg/L | 75 | 74.6 | 84.7 | 85.7
Chromium (Cr)-Total | mg/L | <0.00050 | <0.00050 | 0.00266 | 0.00242
Cobalt (Co)-Total | mg/L | 0.0413 | 0.0409 | 0.00447 | 0.00539
Copper (Cu)-Total | mg/L | 0.00479 | 0.00471 | 0.00361 | 0.0038
Iron (Fe)-Total | mg/L | 0.054 | 0.045 | 0.92 | 1.6
Lead (Pb)-Total | mg/L | <0.000050 | <0.000050 | 0.00049 | 0.000494
Lithium (Li)-Total | mg/L | 0.0039 | 0.0038 | 0.0026 | 0.0027
Magnesium (Mg)-Total | mg/L | 28.1 | 28.8 | 38.6 | 39.8
Manganese (Mn)-Total | mg/L | 0.0677 | 0.0672 | 0.0418 | 0.0326
Molybdenum (Mo)-Total | mg/L | 0.000648 | 0.00063 | 0.000462 | 0.000432
Nickel (Ni)-Total | mg/L | 0.155 | 0.157 | 0.0379 | 0.0395
Potassium (K)-Total | mg/L | 3.34 | 3.38 | 6.23 | 6.71
Selenium (Se)-Total | mg/L | 0.000404 | 0.000508 | 0.000478 | 0.000469
Silver (Ag)-Total | mg/L | 1.5e-05 | 1.3e-05 | 1.8e-05 | 1.5e-05
Sodium (Na)-Total | mg/L | 11.1 | 10.8 | 17 | 18
Strontium (Sr)-Total | mg/L | 0.185 | 0.184 | 0.281 | 0.274
Thallium (Tl)-Total | mg/L | <0.000010 | <0.000010 | <0.000010 | <0.000010
Tin (Sn)-Total | mg/L | <0.00010 | <0.00010 | <0.00010 | <0.00010
Titanium (Ti)-Total | mg/L | <0.00030 | <0.00030 | 0.00152 | 0.00149
Uranium (U)-Total | mg/L | 0.000136 | 0.000137 | 5e-05 | 5.2e-05
Vanadium (V)-Total | mg/L | <0.00050 | <0.00050 | 0.00094 | 0.00089
Zinc (Zn)-Total | mg/L | <0.0030 | <0.0030 | 0.005 | 0.0077
^ Indicates duplicate sample.
Sampling Locations:
BOS8A - 13W 441232 7505523
BOS8B - 13W 441264 7505469
BOS8D - 13W 441356 7505403

## BOS9
Sample ID |  | BOS9 | BOS9 | Part D Item 6
ALS ID |  | YL2300566-001 | YL2300566-002 | Maximum Average Concentration | Maximum Concentration in Any Grab Sample
Date Sampled |  | 2023-06-03 12:00 | 2023-06-03 12:00
Parameter | Units | Water | Water
Conductivity | uS/cm | 64.1 | 63.8
pH | pH | 6.8 | 7.01 | 6.5-9.0
Total Suspended Solids | mg/L | 5.8 | <3.0 | 15 | 30
Ammonia, Total (as N) | mg/L | 0.0154 | 0.0148
Chloride (Cl) | mg/L | 4.45 | 4.44
Nitrate (as N) | mg/L | 0.0864 | 0.0823 | 130 | 260
Sulfate (SO4) | mg/L | 12.4 | 12.4
Aluminum (Al)-Total | mg/L | 0.101 | 0.132
Antimony (Sb)-Total | mg/L | 0.00037 | 0.00037
Arsenic (As)-Total | mg/L | 0.0114 | 0.0111 | 0.05 | 0.1
Barium (Ba)-Total | mg/L | 0.00142 | 0.00164
Beryllium (Be)-Total | mg/L | <0.000100 | <0.000100
Boron (B)-Total | mg/L | <0.010 | <0.010
Cadmium (Cd)-Total | mg/L | <0.0000050 | <0.0000050
Calcium (Ca)-Total | mg/L | 6.17 | 6.25
Chromium (Cr)-Total | mg/L | 0.00156 | 0.0011
Cobalt (Co)-Total | mg/L | 0.0027 | 0.00263
Copper (Cu)-Total | mg/L | 0.00133 | 0.00132 | 0.02 | 0.04
Iron (Fe)-Total | mg/L | 0.198 | 0.191
Lead (Pb)-Total | mg/L | 0.000259 | 0.000245 | 0.01 | 0.02
Lithium (Li)-Total | mg/L | <0.0010 | <0.0010
Magnesium (Mg)-Total | mg/L | 2.19 | 2.17
Manganese (Mn)-Total | mg/L | 0.0132 | 0.0129
Molybdenum (Mo)-Total | mg/L | 7.8e-05 | 8.8e-05
Nickel (Ni)-Total | mg/L | 0.00891 | 0.00888 | 0.25 | 0.5
Potassium (K)-Total | mg/L | 0.346 | 0.347
Selenium (Se)-Total | mg/L | <0.000050 | 5.7e-05
Silver (Ag)-Total | mg/L | <0.000010 | <0.000010
Sodium (Na)-Total | mg/L | 1.86 | 1.77
Thallium (Tl)-Total | mg/L | <0.000010 | <0.000010
Tin (Sn)-Total | mg/L | <0.00010 | <0.00010
Titanium (Ti)-Total | mg/L | <0.00390 | <0.00180
Uranium (U)-Total | mg/L | 6.6e-05 | 6.5e-05
Vanadium (V)-Total | mg/L | 0.0009 | 0.00094
Zinc (Zn)-Total | mg/L | 0.0146 | 0.014 | 0.3 | 0.6
Oil and Grease | mg/L | <5.0 | <5.0 | 5 | 10
Oil And Grease (Visible Sheen) |  | Absent | Absent | No visible sheen | No visible sheen
Bold indicates exceedance of Part D Item 6 Maximum Concentration
^ Indicates duplicate sample.