Final Technical Review 

Done by:  
David Hohnstein

Date:  
January 23, 2003

Licence:  
NWB1HOP0207  Modification of Waste Disposal – RBC Upgrade


	CONTACT INFORMATION
	Contact:
	Hugh R. Wilson

	
	Position:
	Manager, Environmental Affairs

	
	Company:
	Miramar Hope Bay Limited

	
	Address:
	300-889 Harbourside Drive

	
	Address:
	North Vancouver, BC     V7P 3S1

	
	Tel:
	(604) 985-2572 or 1.800.663.8780

	
	Fax:
	(604) 980-0731

	
	Email:
	Hugh_r_wilson@hotmail.com or

hwilson@miramarmining.com 

	

	PROJECT SPECIFICS 
	YES
	NO
	COMMENT

	Is the application complete?

Form, questionnaire, maps
	   X
	 
	No manufacturer’s design specs included other than what was mentioned in the letter.  Email from H. Wilson indicated that it was designed for 130 person camp where the previous was for about 60-80.

	Other permits in place
	   X
	
	

	Conform to LUP   
	
	
	

	NIRB Screening
	
	
	

	Type of Project

Camp 

Geophysical Sampling

Drilling

Other:
	
	
	

	
	   X
	
	Currently operating with about 70 persons.

	
	   X
	
	

	
	   X
	
	

	
	
	
	

	Location
	
	
	Region:
	West Kitikmeot

	Lat/Long  NTS Maps
	   X
	
	68o 15’ N 106o 45’ W

NTS Map # 77 A/3

	IOL
	
	
	

	Crown
	
	
	

	Time Schedule

Multiple year project
	
	
	Early 2004, brought in by Hercules aircraft

	
	   X
	
	Camp in has been operating seasonally from July-Sept each year

	Camp Size
	   X
	
	Licensee indicates that the modification is designed for a 130 person camp; license water use is limited to 50m3/day


Concerns Identified:

For Licensee information, see project specifics above.

	Waste Disposal
	
	
	
	

	Part E
	Design
	
	
	The new RBC unit is designed for 130 persons or a maximum hydraulic loading of 16,250L/day (33 usgpd/person).  The current system is designed for about 70.

	Item 2
	Disposal
	
	
	Condition already in place to control sewage and greywater treatment

	 Item 3
	Holding
	
	
	Condition to provide staged holding of effluent

	Item 4
	Monitoring
	
	
	Provides for some background monitoring requirements on effluent and input to Windy Lake

	Item 5
	Erosion
	
	
	Condition to minimize surface erosion in the discharge area

	Item 6
	Sludges
	
	
	Removed, contained and transported to Boston camp for disposal (sump)

	
	
	
	
	

	Item 7
	Alternate sludge disp.
	
	
	Must apply to the Board

	
	
	
	
	

	
	
	
	
	


Summary

License NWB2HOP0207 reflects the most current conditions and addresses the disposal of sewage and greywater utilizing the RBC treatment facility.  The modifications planned are simply an upgrade to the existing treatment and can be addressed through the current license conditions.

	Regulatory Timeline

	Application Received:
	23 Sept 2003
	

	Prelim Tech Review Completed:
	04DEC2003
	  

	NPC Conformity Review Received:
	
	

	NIRB Screening Received:
	
	

	DIAND Comments Received
	
	

	EC Comments Received
	November 27, 2003
	No Concerns; inform of plans to dispose of old RBC and any sludge contained.

	DFO Comments Received
	November 18, 2003
	No Concerns

	Final Tech Review Drafted
	January 23, 2004
	

	Final Tech Review Approved
	
	

	Licence Drafted:
	
	


References


040123NWB1HOP0207 FTR-WindyRBC-ITME



- 1 -

