## Summary Table
2BM-ULU0914 Compliance and Inspection Follow-Up
Inspector's | Comments related to site conditions as found in inspection reports or follow-up correspondence - and status / summary of the issue at present. |  |  | Issue addressed within time frame as directed. | Issue partially addressed or unknown. | Issue unaddressed within time frame as directed.
Observations | 2012 | 2013 | 2014 | 2015 | 2016 | 2017 - Comments
NWNSRTA s.11 USE OF WATER WITHOUT A LICENCE |  |  | 141021 September Monthly Monitoring Rpt: indicates that DMS and WPC Resources were on site September 1-5 2014 to conduct work. This is after the licence expiry. 5 days, 8200L / 8.2 m3 water reported. | Requested clarification on several aspects of the 2014 activities as reported in the August and September (2014) reports. No response was received until Oct 2015. |  | Water use continued after expiry in 2014.
|  |  | WPC Resources led me to believe their work was only conducted in August; WPC's licence was not issued until November 2014 (and does not allow for a camp). | Requested clarification on several aspects of the 2014 activities as reported in the August and September (2014) reports. No response was received until Oct 2015. |  | Appears WPC operated in September 2014 without the benefit of either the 2BM-ULU or the 2BE-HRP licences.
PART D CONDITIONS RELATED TO WASTE DISPOSAL | RBC unit discharging untreated effluent to the lake. |  |  |  |  | Assume that Licensee will manage RBC accordingly when next operational.
|  | Waste storage areas unmarked. |  | Waste and waste storage areas remain unidentified... | Waste and waste storage areas remain unidentified... | Assumed that waste areas remain unmarked.
|  | Barrels found on rock pad. MMG's berm at the airstrip is torn. BCC is responsible for activities conducted on their site. Empty barrels and haz waste remain (2012 sewage at airstrip). All hazardous materials are to be stored in secondary containment. | Hazardous waste remains widespread on site: mine waste pad, barrel storage area beside tank farm, in waste piles east of helipad, and barrels at the airstrip. | Several barrels of hazardous waste and contaminated soil at the mine storage pad. Waste (particularly potentially‐hazardous waste) is not being stored according to the Waste Management Plan. | Waste (particularly potentially‐hazardous waste) is not being stored according to the Waste Management Plan. Unmarked barrels of unidentifiable waste (with staining underneath) remain to the east of the helipad… and at the mine storage pad… there remain several barrels of [potentially] hazardous waste and contaminated soil at the mine storage pad. Conditions remain unchanged in 2016. | Assumed waste is now in containment as per January 2017 correspondence.
|  | Hazardous and human waste is to be removed from site particularly with site in care and maintenance. | Lack of waste backhaul since 2012. |  |  | Assumed unresolved as no backhaul has been reported despite explicit instructions to do so.
|  | Geotech submitted to NWB November 2013. Recommends repairs to berms and liners in 2014. Same repairs as recommended in 2013, but as they were not undertaken, the engineer included a date. | Geotech submitted to NWB November 2013. Recommends repairs to berms and liners in 2014. Same repairs as recommended in 2013, but as they were not undertaken, the engineer included a date. | The liner for the Retention Pond has slipped on the east side and much of the liner is exposed. As identified in the geotechnical inspection, it is not an immediate issue unless that pond is required for use. |  | Assumed unresolved as no significant maintenance work has been carried out.
|  | 130430 CMP states that BCC will carry out repairs to the tank farm berms in 2014. |  |  |  | Assumed unresolved as no significant maintenance work has been carried out.
|  | 130430 WMP indicates that the incinerator needs repairs and will be retrofitted or upgraded prior to the next exploration season. |  |  |  | Assumed unresolved as no significant work has been carried out, however, incinerator was used in recent years.
|  |  |  | Mitigation measures are not being implemented to limit the impacts of this site on the receiving environment. | No mitigation measures have been put in place to address impacts of this site on the receiving environment: monitoring activities, implementation of the spill contingency plan, sediment control measures etc. | Partially addressed: spill boom deployed at fuel storage pad; silt curtains installed at select wash-outs along the road.
|  |  |  | Wash‐outs were noted along the road between the airstrip and camp. | Road wash-outs as described in the 2015 report have not been addressed. Culverts may require maintenance to restore flow of streams. No sediment control measures have been implemented since 2015 inspection. | Partially addressed: spill boom deployed at fuel storage pad; silt curtains installed at select wash-outs along the road.
[5 empty] | The water in the portal entrance was very high at the time of the inspection. Discharge lines were set up from the portal, assumedly to conduct a discharge, however, no samples or notification of discharge had been provided to me at that time (or was subsequently provided). The liner of the retention pond has slipped at one end. If the licensee intends to use this pond, which seems likely by the pump and hoses leading into it, the liner should be repaired. | Assumed unresolved as no work has been reported.
PART E CONDITIONS RELATED TO SPILLS AND SPILL CONTINGENCY | Unsatisfactory storage of chemicals and hazardous materials. |  |  |  | As per the 2015 report: “Waste and waste storage areas remain unidentified and waste (particularly potentially‐hazardous waste) is not being stored according to the Waste Management Plan. Unmarked barrels of unidentifiable waste (with staining underneath) remain to the east of the helipad… and at the mine storage pad… there remain several barrels of [potentially] hazardous waste and contaminated soil at the mine storage pad…” Conditions remain unchanged in 2016. | Hazardous materials: Assumed to be resolved per January 2017 update from BCC. Pending inspection.
| Fuel transfers occurring without drip tray. | Numerous spills noted on-site. Spills on-site should be addressed at the time of the spill. Two leaking barrels were found (one outside of containment). | Lack of containment, monitoring, and cleanup of spills. Fuel is migrating off the storage pad and down-slope. | Spills are not being addressed in accordance with the Spill Contingency Plan or the Licence. The contamination spreading from the fuel storage pad/apron was raised as an issue in 2014, and has worsened since that time. | As per inspection reports from 2013-2015, the hydrocarbon contamination spreading from the fuel storage pad/apron has not been addressed. Nor has it yet been reported. A GPS track of the visible perimeter of the stain was taken, and calculated the visible affected area as 2288.2 ft2 (212.5m2). The affected area below the sand surface is unknown at this point, but is likely the depth of the active layer. Shallow samples of the stained sand were taken at 25 m and 32 m downslope of the fuel storage pad, and confirm F3 (C16-C34) concentrations of 3740 and 9690 mg/kg respectively (2.2x and 5.7x the CCME Tier 1 levels for coarse-grained soils (commercial/industrial)). F4 (C34-C50) concentration of the second sample also surpasses CCME Tier 1 level for residential/parkland at 2970 mg/kg, 32 m downslope of the fuel storage pad. These F3 levels are HIGHER than the samples taken in 2015 which were taken at 13 m downslope of the fuel storage pad. Staining within the storage pad is also more pronounced than in 2015. | Spill management: Unresolved - large spill from fuel storage pad has not been reported, sampled, or remediated. Spill boom was installed around fuel storage pad to prevent further product from migrating down-slope.
| Fuel and pumps placed within 30m of water. |  |  |  |  | Fuel storage and pumps: tbd when site is active
PART I CONDITIONS RELATED TO ABANDONMENT, RESTORATION, TEMPORARY CLOSING |  | Drill sites are not adequately restored. |  | Drill holes have not been restored to pre‐disturbance conditions. | As per the 2015 report: “Drill holes have not been restored to pre‐disturbance conditions. Numerous drill collars are visible in the vicinity of the site. This was identified in the 2013 inspection and has not yet been addressed.” A list of drill holes was submitted to the Inspector in November 2015. In the accompanying report, the Licensee states “As far as we are aware all holes have been reclaimed.”, despite photographs and reports that I have submitted from 2013 - 2015 that demonstrate otherwise. | Unresolved - list provided but request not satisfied: holes not reclaimed
[5 empty] | As a result of lack of maintenance, site conditions are deteriorating. The large Quonset has torn open, exposing the materials and equipment stored therein. | Uncertain. No comment received.
[5 empty] | The dock at the West Lake water intake facility is in disrepair, and at risk of becoming debris in the lake. It should be removed before the situation worsens. | Unresolved.
PART J CONDITIONS RELATED TO MONITORING |  | Monitoring of the site is to continue as per licence requirements under Part J, unless documentation can be provided to the Inspector showing dispensation from the Board to suspend monitoring at the site. Monthly reports have not been submitted in the required timelines (eg-April and May received July 30) and do not speak to the actual required monitoring. | Lack of monitoring; inadequate reporting in monthly reports. | No monitoring reports have been filed on the NWB FTP site since March 2015. No 2014 monitoring results were submitted with the annual report. | No results were submitted for monitoring of ULU-8, which should be sampled twice annually during open water period. | Assumed non-compliant due to lack of reporting and BCC's lack of presence on-site.
OTHER | 2012 Annual report does not address Part B Item 8 (g); actions to address concerns detailed in the Inspection reports. |  | Annual report deficient. |  |  | TBD for 2016
REPORTING /ADMIN | Operating with outdated plans. |  |  |  |  | Resolved
|  |  | No notification submitted under Part H Item 1 that site would be activated. No mention was made to inspector during July visit that site would be active in August. |  |  | Resolved
|  |  |  | QA/QC plan within 60 days following licence issuance with a confirmatory letter from an accredited laboratory |  | Received
Inspector's instructions | Specific instructions given to BCC in inspection reports, and whether those instructions were carried out as directed: |  |  | Issue addressed within time frame as directed. | Issue partially addressed or unknown. | Issue unaddressed within time frame as directed.
| 2012 | 2013 | 2014 | 2015 | 2016 | 2017 - Summary and Status
Sewage/Human waste | Effluent immediately diverted to lined mine containment sump until discharge criteria are met or alternative disposal for human waste is implemented. | Sewage at the airstrip is to be backhauled in 2013, and as much hazardous waste as possible removed from site. |  |  | Repair to portal containment pond, in case it is required in the future | Assumed compliant: Licensee has employed other methods to dispose of sewage when the site is minimally staffed.
Hazardous Waste | All oils & haz waste to be collected and placed in containment by 31 July. | Hazardous waste is to be backhauled. | All new hazardous waste is to be backhauled in the year it is created to prevent the accumulation of waste to unmanageable levels. |  |  | Non-compliant: no backhaul has been reported. Licence conditions indicate that hazardous waste is to be backhauled.
|  |  | All hazardous materials at site to be placed within secondary containment. Open barrels to be covered. By September 30 2014. | All hazardous (and unknown) waste is to be moved into SOUND secondary containment that meets the definition of ‘secondary containment’ in the current licence 2BM‐ULU1520. This is to be completed by June 30, 2016. | All hazardous (and unknown) waste is to be moved into SOUND secondary containment that meets the definition of ‘secondary containment’ in the current licence 2BM‐ULU1520. * | Assumed compliant, if all waste is now in containment as per January 2017 correspondence. Pending inspection.
Waste Storage and Handling |  | Waste storage areas are to be clearly identified. |  |  |  | Assumed non-compliant: that waste areas remain unmarked.
|  | Waste is to be clearly identified. |  |  |  | Unknown.
Fuel storage | Fuel pump set >30 m back from water and photos by 24 July. | All fuel is to be stored in secondary containment, and covered to prevent water accumulation in the containment during periods of inactivity. | All hazardous materials at site to be placed within secondary containment. Open barrels to be covered. By September 30 2014. | All barrels of fuel are to be moved into SOUND secondary containment that meets the definition of ‘secondary containment’ in the current licence 2BM‐ULU1520. This is to be completed by June 30, 2016. | All barrels of fuel are to be moved into SOUND secondary containment that meets the definition of ‘secondary containment’ in the current licence 2BM‐ULU1520. * | Assumed compliant: that all fuel and haz mat are now in secondary containment per January 2017 update from BCC. Pending inspection.
|  | MMG berm is to be repaired or replaced, or MMG fuel removed from site. |  |  |  | Resolved.
Fuel handling | Fuel transfers to occur over drip trays. |  |  |  |  | Assumed resolved.
SPILLS |  | Spill at the airstrip is to be cleaned up as per Spill Contingency Plan. | Spills around site are to be addressed as per Spill Plan. Contaminated soil is to be backhauled. By September 30 2014. | Spills are to be reported and addressed according to the approved Spill Contingency Plan. | Spills are to be reported and addressed according to the approved Spill Contingency Plan. | Non-compliant. BCC has failed to appropriately manage the fuel leaking from the storage pad since 2014.
|  |  |  | a) stop the flow of hydrocarbons from the fuel storage pad | a) stop the flow of hydrocarbons from the fuel storage pad | Partially addressed: spill boom deployed at fuel storage pad and old barrels/waste were removed. Fuel remains on the pad, despite the knowledge that it is not containing spilled fuel.
|  |  |  | b) prevent any further migration of hydrocarbons down‐slope from the fuel storage pad | b) prevent any further migration of hydrocarbons down‐slope from the fuel storage pad | Non-compliant. BCC has failed to appropriately manage the fuel leaking from the storage pad and instructions of the inspector since 2014.
|  |  |  | c) remediate the affected area | c) remediate the affected area | Non-compliant. BCC has failed to appropriately manage the fuel leaking from the storage pad and instructions of the inspector since 2014.
O+M | Liners and berms to be assessed in next geotechnical inspection. |  |  |  |  | Assumed incomplete: Geotech was submitted 121127 to NWB. BCC was recommended to cover exposed liners and repair damaged liners. Cover letter indicates that a compliance plan would be developed and plan discussed with the inspector, but no actual work was proposed to implement recommendations. No compliance plan was received. 2013 geotech ecommended repairs to berms and liners in 2014. To my knowledge, no repairs / significant site maintenance has been undertaken.
Monitoring |  | The Monitoring program is to be implemented immediately, or documentation provided to the Inspector by July 31, 2013 that demonstrates authorization of the Board to discontinue Monitoring. | Monthly monitoring during snow-free season is to be implemented (including freshet). This includes monitoring of waste + fuel as well as implementing the monitoring program as per the licence. |  |  | Non-compliant. Monitoring was not undertaken as required for the last several years.
|  |  |  | Establishment (and regular maintenance) of sediment control measures to prevent further sediment loading of streams that have been affected by road deterioration. These measures are to be put in place at freshet 2016. | Establishment (and regular maintenance) of sediment control measures to prevent further sediment loading of streams that have been affected by road deterioration. These measures are to be put in place at freshet (now 2017). | Partially addressed. Silt curtains installed and road maintenance undertaken at two wash-outs along the road. Regular inspections and maintenance are required.
[5 empty] | Conduct a visual assessment of all culverts on site, and provide a report including: GPS coordinates of each, culvert condition, whether flow is possible or obstructed in any way. This report shall be submitted to the inspector by September 30, 2017. | To be undertaken 2017.
Progressive reclamation |  | A timeline to address progressive reclamation of drill sites is to be prepared. |  | A complete list of drill holes (with GPS coordinates) associated with this project (drilled by past and current operators) is to be provided to the Inspector. Please identify any holes that are known to be reclaimed according to the terms of the licence. This list is to be provided by January 31, 2016. | Conduct a visual inventory of all the known drill holes, as per the list provided to the inspector in 2015 (approximately 365 holes). Each drill hole shall be inspected for compliance with Part I items 13 and 15, and any other relevant conditions of the licence. The Licensee shall reclaim each hole that does not satisfy these conditions to a pre-disturbed state, including contouring, cutting of drill casings or collars flush with the ground, and any other remediation required (spills, debris etc). The Licensee shall complete this work over the next one (1) to three (3) years, with a minimum of one third to be completed each year, beginning in 2017. A table shall be submitted to the inspector by June 01 of each year, beginning in 2017, that lists the drill holes to be inspected in that year by hole number and location, and the dates the work will be undertaken. The Licensee shall submit by September 30, of each year, beginning in 2017, a table that describes each drill hole completed by number; location; whether it satisfied the licence conditions; and where no, confirmation that the hole was reclaimed. Photographs before and after are encouraged. Work is to be conducted in the snow-free season. | To be undertaken 2017.
[5 empty] | Removal of the dock and any structures that may become waste in the water | To be undertaken 2017.
Plans / Reporting | Current CM plan, Waste Mgmt Plan to Inspector by 24 July. |  |  | revised QA/QC plan and letter as required by the licence are to be submitted to the Board by November 30, 2015. |  | Compliant.
Inspection Follow-Up |  | Required actions are to be completed and a report submitted to the Inspector by September 30 2013. Report received, but items not addressed to the satisfaction of the Inspector. | A report with the details of required actions above is to be submitted to the inspector by October 31, 2014. Received December 9 at the request of the Inspector. | Compliance work to be completed by July 31, 2016 and a confirmatory report submitted to the inspector by August 15, 2016. BCC notified the inspector on September 6 that they had not had access to site, and now had a temporary LUP. BCC did not attend site until September 2016, and then only partially completed the work. | Provide confirmation in writing by December 15, 2016, of those activities carried out in 2016 (a list of priorities was sent to BCC on September 9, 2016). Received January 19, 2017. Work partially completed. Response was only received after prompting BCC. The rest of the activities are to be carried out in 2017. | I have discussed the outstanding compliance issues and environmental hazards at the Ulu site with Wynter at the KitIA, and I will be working with her to ensure that, even if tenure issues remain unresolved in 2017, there will be a mechanism to ensure that BCC/WPC can carry out their obligations under this water licence. The fact remains that these issues should have been addressed prior to 2016 as they were identified in several past inspection reports. As with the issues at Lupin, I will issue a Direction if/when necessary but I would hope that the project can be brought into compliance without entering the enforcement realm.
|  |  |  | Response to my questions of January 16 and 19, 2015, by November 30, 2015. Response received October 30 - 9 months after request. | Review the 2013-2015 inspection reports, and create a work plan for 2017 that will address all of the outstanding work, and including the items identified below. This work plan is to be submitted to the Inspector for review and approval by January 31, 2017. Failure to address these deficiencies according to the approved plan will result in enforcement action. No workplan has been received as of February 9, 2017. | Here is a summary of the outstanding work and compliance issues at site. Workplan to be sumitted to the Inspector for review by February 28, 2017.