## Slide 1: ᓄᓇᕗᒻᒥ ᐃᒪᓕᕆᔩᑦ ᑲᑎᒪᔨᖏᑕ ᑲᑎᒪᓂᖓ
ᐃᒥᕐᒧ ᐱᔪᓐᓇᐅᑎᖓ ᓄᑖᙳᕆᐊᖅᑕᐅᓂᖓ ᐊᒻᒪ ᐋᖅᑭᒋᐊᖅᑕᐅᓂᖓ
ᐊᕐᕕᐊᑦ
3AM-ARV----
Nunavut Water Board Public Meeting
Water Licence Renewal and Amendment
Arviat
3AM-ARV----

## Slide 2: ᐱᔪᓐᓇᐅᑕᐅᒌᖅᑐᖅ
Existing Licence

## Slide 3: Water Licence: 3AM-ARV---
This application is for the renewal and amendment of the expired 3AM-ARV1015 licence.
Date of Licence Issuance: August 23, 2010
Expiry of Licence: August 31, 2015
Short Term Renewal: June 16, 2015
Short Term Expiry: February 27, 2016
Scope of Licence:
This Licence allows for the use of Water and disposal of Waste including operation of a
Water Supply Facility, Solid Waste Disposal Facility, Hazardous Waste Storage Area,
Bulky Metals Area, and Sewage Disposal Facility.
ᑖᓐᓇ ᐱᓇᔫᑎ ᓄᑖᖑᕆᐊᖅᑎᑦᑎᓂᕐᒨᖓᔪᖅ ᐋᖅᑭᒋᐊᖅᑕᓄᓪᓗ ᐃᓱᓕᔾᔪᔨᔪᒧᑦ 3AM-ARV1015 ᐱᔪᓐᓇᐅᑎ.
• ᐅᓪᓗᖓ ᐱᔪᓐᓇᐅᑎᑖᕐᕕᒋᓯᒪᔭᖓ: ᐋᒡᒌᓯ 23, 2010
• ᐱᔪᓐᓇᐅᑎᐅᑉ ᐃᓱᓕᕝᕕᑦᓴᖓ: ᐋᒡᒌᓯ 31, 2015
• ᓇᐃᑦᑐᒥᒃ ᐃᓱᓕᕝᕕᒃᓴᓕᒃ ᓄᑖᖑᕆᐊᖅᑎᑦᑎᓂᕐᒧᑦ: ᔫᓂ 16, 2015
• ᓇᐃᑦᑐᒥᒃ ᐃᓱᓕᕝᕕᒃᓴᓕᒃ ᐃᓱᓕᕝᕕᖓ: ᕕᕗᐊᕆ 27, 2016
• ᖃᓄᐃᓕᖓᓂᖓ ᐱᔪᓐᓇᐅᑎᖓᑕ:
ᑖᓐᓇ ᐱᔪᓐᓇᐅᑎ ᐱᔪᓐᓇᖅᑎᑦᑎᔪᖅ ᐊᑐᕐᓗᓂ ᐃᒪᕐᒥᑦ ᐊᒻᒪ ᐱᓯᒪᔪᓐᓃᕐᓂᖅ ᐊᑐᒐᒃᓴᐅᔪᓐᓃᖅᑐᒥᒃ ᐃᒪᕐᒥᑦ ᐃᓚᐅᓗᓂ ᐊᐅᓚᓂᖓ
ᐃᒪᖃᕐᕕᒃ, ᐊᒃᑕᕐᕕᖃᕐᕕᒃ, ᓴᓃᑦ ᐅᓗᕆᐊᓇᖅᑐᑦ ᐃᓕᓯᕕᖓ,
ᓴᕕᕋᔭᖕᓄᑦ ᐃᓕᓯᕕᒃ, ᐊᒻᒪ ᑭᓈᓗᖃᕐᕕᒃ,
ᐃᒥᕐᒧᑦ ᐱᔪᓐᓇᐅᑎᖓ: 3AM-ARV----

## Slide 4: Water Licence: 3AM-ARV---
In the absence of an active licence Arviat has continued to:
Report quantities of water withdrawn &wastewater deposited
Improve the management of solid waste
Understand studies to improve water and waste infrastructure
Conduct monitoring program sampling
Engage in regular communication with the CIRNAC Inspector on compliance issues
Completed Projects:
Additional raw water reservoir cell
Ongoing Projects
Upgrade and expansion of the wastewater lagoon
Upgrade and expansion of the solid waste site
ᐱᑕᖃᙱᑎᓪᓗᒍ ᐊᑐᖅᑐᒥᒃ ᐱᔪᓐᓇᐅᑎᒥᒃ ᐊᕐᕕᐊᑦ ᑲᔪᓯᔪᖅ:
ᑎᑎᕋᕐᓗᒋᑦ ᖃᓄᑎᒋᐅᓂᖏᑦ ᐃᒻᒥᕆᔾᔪᑕᐅᔪᑦ ᐃᒥᑦᑎᐊᕙᐅᙱᑦᑐᓂᒃᓗ ᐃᓕᔭᐅᔪᓂᒃ
ᐱᐅᓯᒋᐊᕐᓗᒍ ᐊᐅᓚᑦᑎᓂᖅ ᐃᒪᕐᒥᒃ
ᑐᑭᓯᓗᒍ ᖃᐅᔨᔭᐅᓇᓱᒍᑎᑦ ᐱᐅᓯᒋᐊᕐᓗᒍ ᐃᒪᖅ ᐃᒥᑦᑎᐊᕙᐅᙱᑦᑐᕐᓗ ᒪᑭᒪᐃᓐᓇᕈᑎᒃᓴᓂᑦ
ᐱᓕᕆᐊᖃᕐᓗᓂ ᖃᐅᔨᓴᐃᓐᓇᕈᑎᓄᑦ ᐱᓕᕆᐊᒃᓴᒥᑦ ᖃᐅᔨᓴᕈᑎᒃᓴᓂᑦ
ᐃᓚᐅᖃᑕᐅᓗᓂ ᑐᓴᐅᒪᖃᑦᑕᐅᑎᔾᔪᑎᐅᒐᔪᒃᑐᓂᑦ ᑯᐄᓐ ᑭᒡᒐᖅᑐᖅᑎᖓ−ᓄᓇᖃᖅᑳᖅᓯᒪᔪᓕᕆᓂᖅ ᐊᒻᒪ ᐃᓄᓕᕆᔨᑐᖃᒃᑯᑦ ᑲᓇᑕᒥ ᖃᐅᔨᓴᖅᑎ ᒪᓕᑦᑎᐊᕐᒪᖔᑦ ᐱᔾᔪᑎᓄᑦ
ᐱᔭᕇᖅᓯᒪᔪᑦ ᐱᓕᕆᐊᒃᓴᑦ:
ᐃᓚᒃᑲᓐᓂᖓ ᐃᒥᖅᑕᕐᕕᒃ
ᐱᓕᕆᐊᒃᓴᓪᓗᐊᑕᐃᑦ
ᓄᑖᖑᕆᐊᕈᑎᑦ ᐊᖏᒃᓕᒋᐊᕈᑎᓪᓗ ᑭᓈᓗᖃᕐᕕᖕᓂ
ᓄᑖᖑᕆᐊᕈᑎᑦ ᐊᖏᒃᓕᒋᐊᕈᑎᓪᓗ ᐊᒃᑕᕐᕕᖕᓂ
ᐃᒥᕐᒧᑦ ᐱᔪᓐᓇᐅᑎᖓ: 3AM-ARV----

## Slide 5
ᒪᑭᒪᔾᔪᑎᑦ
Infrastructure

## Slide 6: Background
Wolf Creek is the domestic water supply for the Municipality of Arviat, approximate population of 2,657 (2016 Census)
The watershed is frozen for seven to nine months a year; therefore, a 3- cell raw water reservoir with capacity 235,393 m3 must be adequately supplied through an 8 km transmission line prior to freeze-up each year. The first cell of the reservoir was built and has been in use since 1988, the second cell was constructed in 1998, and the third cell in 2019.
The Wolf Creek 2019 Hydrologic Assessment report indicated that only 0.2% of water is being diverted for the reservoir resupply which is below the Fisheries and Oceans Canada limits to preserve fish passage.
ᑰᖓᓂ ᑖᓐᓇ ᐃᓄᓐᓄᑦ ᐃᒥᖅᑖᕐᕕᐅᖃᑦᑕᖅᑐᖅ ᕼᐋᒻᒪᓚᒃᑯᓄᑦ ᓴᓪᓕᖅᒥ, ᐃᓄᒋᐊᓐᓂᖃᑦᑐᖅ 2,657 (2016-ᒥ ᓈᓴᖅᑕᐅᓯᒪᔪᑦ)
ᑖᓐᓇ ᖁᐊᖑᖃᑦᑕᖅᑐᖅ ᑕᖅᑭᓄᑦ 7ᓂᑦ 9ᓄᑦ ᐊᕐᕌᒎᑉ ᐃᓗᐊᓂ, ᑕᐃᒪᐃᓐᓂᖓᓄᑦ, ᐱᖓᓱᐃᓕᖓᔪᖅ ᐃᒥᕐᑕᖅᕕᒃ ᐃᓂᖃᖅᑎᒋᓪᓗᓂ 235,393 m3 ᓈᒻᒪᒋᔭᖓᓂ ᐱᖃᖅᑎᑕᐅᔭᕆᐊᓕᒃ ᑕᐃᑰᓇ 8 ᑭᓚᒦᑕ ᐃᒥᖅᑕᕐᕕᖕᒧᑦ ᖁᐊᓚᐅᙱᓐᓂᖓᓂᒃ ᐊᕐᕌᒍᑕᒫᑦ. ᓯᕗᓪᓕᖅ ᐃᒥᕐᑕᖅᕕᒃ ᓴᓇᔭᐅᓚᐅᖅᓯᒪᔪᖅ ᐊᑐᖅᑕᐅᖏᓐᓇᖅᓱᓂᓗ 1988-ᒥᓂ, ᐊᐃᑉᐸᖓ (ᐃᒪᓕᕆᓂᖅ ᑲᓲᑎᓯᒪᑦᓱᓂ) ᓴᓇᔭᐅᓯᒪᔪᖅ 1998-ᒥ, ᐱᖓᔪᖓᓪᓗ 2019-ᒥ.
ᐊᒪᕈᖅ ᑰᕈᖅ 2019 ᐃᒥᕐᓄᑦ ᖃᐅᔨᓴᕈᑎ ᐅᓂᒃᑳᖅ ᓇᓗᓇᐃᖅᓯᓪᓗᓂ ᐃᒪᓐᓇᑐᐃᓐᓇᖅ 0.2% ᐃᒪᕐᒥ ᐅᑎᕆᐊᖅᑎᑕᐅᔪᓂ ᐃᒥᖅᑕᕐᕕᖃᒃᑲᓐᓂᕈᑎᓂ ᑐᖔᓃᑦᑐᖅ ᐃᒪᕐᒥᐅᑕᓕᕆᔨᒃᑯᑦ ᑲᓇᑕᒥ ᐃᓱᖃᖅᑎᑕᖓᓄᑦ ᔭᒐᑎᑦᑕᐃᓕᓗᒍ ᐃᖃᓗᐃᑦ ᐊᖅᑯᑎᖏᑦ.
ᐱᓕᕆᐊᖑᓯᒪᔪᑦ

## Slide 7: Background
A passive lagoon has received wastewater since 2005. The 37,960 m3 lagoon acts as a holding cell during the frozen month and effluent freely flows out upon thaw. Most of the effluent treatment is attributed to the wetland treatment area.
The 7.3-hectare wetland treatment area directs effluent flow away from the municipality and towards Hudson Bay at the end of the wetland.
A new 2-cell lagoon project is underway that will upgrade the current lagoon and construct an adjoining cell. The new capacity is sized to accept wastewater for 12 month for the next 20 years. It will also be sized to hold sludge for the lifespan of the asset.
2 legacy abandoned lagoon cells adjacent to the active lagoon cells require remediation.
ᐱᔪᓐᓇᖅᑎᑦᑎᔾᔪᑎ ᑭᓈᓗᖃᐅᑎ ᐱᓪᓗᑎᒃ ᑭᓈᓗᖕᓂᑦ ᑕᐃᒪᙵᑦ 2005. 37,960 m3 ᑭᓈᓗᖃᕐᕕᐅᖃᑦᑕᖅᑐᖅ ᐅᑭᐅᖑᑎᓪᓗᒍ ᐊᒻᒪᓗ ᑭᓈᓗᒃ ᑯᕕᔭᐅᓂᖓ ᑰᒻᒧᑦ ᐃᒫᓄᓪᓘᓐᓃᑦ ᒪᙳᕋᐃᒻᒪᑦ. ᐃᓚᖓ ᑭᓈᓗᒃ ᑯᕕᔭᐅᓂᖓ ᑰᒻᒧᑦ ᐃᒫᓄᓪᓘᓐᓃᑦ ᓴᓗᒻᒪᖅᓴᖅᑕᐅᓂᖅ ᑐᓂᔭᐅᓪᓗᓂ ᐃᒪᖃᕐᓂᐅᔪᕐᒥᒃ ᐱᓕᕆᐊᖃᕐᕕᐅᔪᒧᑦ
7.3-ᓄᓇᐅᑉ ᐆᑦᑐᖅᓯᒪᓂᖓ ᐃᒪᖅᓱᖃᓗᐊᕈᓐᓃᖅᑎᓪᓗᒍ ᐊᕙᑎᖓ ᑐᑭᒧᐊᒃᑎᑦᑎᔪᖅ ᑭᓈᓗᒃ ᑯᕕᔭᐅᓂᖓ ᑰᒻᒧᑦ ᐃᒫᓄᓪᓘᓐᓃᑦ ᑰᒃᓗᓂ ᓄᓇᖓᓂ ᑕᐃᑯᖓ ᑲᖏᖅᓱᐊᓘᑉ ᐃᓗᐊ ᐃᓱᖓᓄᑦ ᐃᒪᖅᓲᑉ.
ᓄᑖᖅ ᒪᕐᕈᐃᓕᖓᔪᖅ ᑭᓈᓗᖃᕐᕕᖕᒧᑦ ᐱᓕᕆᐊᒃᓴᖅ ᐱᒋᐊᕐᓂᐊᖅᑐᖅ ᓄᑖᖑᕆᐊᖅᑎᑦᑎᓗᓂ ᒫᓐᓇ ᑭᓈᓗᖃᕐᕕᖕᒥᑦ ᐱᓕᕆᐊᖃᕐᓗᑎᒃᓗ ᑲᑎᙵᔪᒥᒃ ᐃᓂᒃᓴᒥᑦ. ᐃᓂᖃᕐᕕᐅᓕᓵᖅᑐᖅ ᐊᖏᓂᖃᖅᑎᑕᖅ ᓈᒻᒪᒋᓗᒍ ᐃᒪᕐᓘᑎᒃᑯᕕᖕᒧᑦ 12 ᑕᖅᑭᓄᑦ ᑭᖑᓂᖏᓐᓄᒃ 20 ᐊᕐᕌᒍᓄᑦ. ᐊᖏᓂᖃᖅᑎᑕᐅᓂᐊᕐᒥᔪᖅ ᐱᓯᒪᐃᓐᓇᕈᓐᓇᕐᓗᑎᒃ ᐊᑐᕈᓐᓇᐃᓐᓇᕈᑎᒃᓴᖓᓄᑦ ᐱᖁᑎ.
ᒪᕐᕉᒃ ᐊᑐᕐᓂᑯᑐᖃᕐᓂ ᐊᑐᖅᑕᐅᔪᓐᓃᖅᑑᒃ ᑭᓈᓗᖃᕐᕖᒃ ᓴᓂᖏᓐᓃᑦᑐᑦ ᑭᓈᓗᖃᕐᕕᖕᓂ ᓄᑖᖑᕆᐊᖅᑕᐅᕐᔪᐊᕆᐊᓕᑦ.
ᐱᓕᕆᐊᖑᓯᒪᔪᑦ

## Slide 8: Background
Arviat’s primary solid waste site has been in use since 1977 with an area 160 x 200 within the fenced containment berms. The metal waste area has an approximate area of 40,000 m2.
A metals shredder was purchased by the municipality in 2017. Since operation, approximately 25% of the metals have been shredded. Non-polluted shredded metal is used as cover on the landfill site with gravel.
Arviat has a summer-long clean up program, inclusive of 12 summer hires and 25 students.
There is an ongoing solid waste improvement project managed by CGS. The project will improve compliance, capacity, and evaluate the abandoned lagoon cells for suitability to be remediated and upgraded to act as an extension to the current landfill.
ᐊᕐᕕᐊᑦ ᐊᒃᑕᑰᓯᖃᕐᕕᖓᑕ ᐃᓂᖓ ᐊᑐᖅᓯᒪᓕᖅᑐᖅ ᑕᐃᒪᙵᑦ 1977 ᐃᒪᓐᓇᐅᑎᒋᓪᓗᓂ 160 x 200 ᓴᐴᓗᑕᖃᖅᖢᓂ ᑰᒃᕕᓕᐊᖑᓯᒪᔪᒥᒃ. ᓴᕕᕋᔭᖕᓄᑦ ᐊᒃᑕᕐᕕᒃ ᐃᒪᓐᓇᐸᓘᑎᒋᔪᖅ 40,000 m2.
ᓴᕕᕋᔭᖕᓄᑦ ᓯᖁᑦᑎᕆᔾᔪᑎ ᓂᐅᕕᖅᑕᐅᓚᐅᖅᑐᖅ Hᐋᒻᒪᓚᒃᑯᖓᓂ 2017-ᒥ. ᐊᐅᓚᓂᖃᓕᖅᑎᓪᓗᒍ, ᐃᒪᓐᓇᐸᓗᒃ 25% ᓴᕕᕋᔭᐃᑦ ᓯᖁᑦᑎᖅᑕᐅᓯᒪᓕᖅᑐᑦ. ᓱᕈᖅᓴᐃᔭᙱᑦᑐᑦ ᓯᖁᑦᑎᖅᑕᐅᓯᒪᔪᑦ ᓴᕕᕋᔭᑦ ᐊᑐᖅᑕᐅᓪᓗᑎᒃ ᕐᑳᕆᓪᓗᓂᐅᒃ ᓄᓇᖓᑕ ᐃᓂᖓᓂ ᑐᐊᐸᖃᕐᖢᓂ.
ᐊᕐᕕᐊᓂ ᐊᐅᔭᓕᒫᒃᑯᑦ ᓴᓗᒻᒪᖅᓴᐃᓂᕐᒥ ᐱᓕᕆᐊᒃᓴᓕᑦ, ᐃᓚᐅᑎᑦᑎᓪᓗᓂ 12−ᓄᑦ ᐊᐅᔭᒃᑯᑦ ᐃᖅᑲᓇᐃᔭᖅᑎᑦᑎᓂᕐᒥᒃ ᐊᒻᒪ 25−ᓂᑦ ᐃᓕᓐᓂᐊᖅᑎᓂᑦ.
ᐊᒃᑕᑯᓄᑦ ᐱᐅᓯᒋᐊᕈᓐᓇᕈᑎᐅᔪᓄᑦ ᐱᓕᕆᐊᒃᓴᖅᑕᓕᒃ ᐊᐅᓚᑕᐅᓪᓗᓂ ᓄᓇᓕᖕᓂ ᒐᕙᒪᒃᑯᓐᓂᓗ ᐱᔨᑦᑎᕋᖅᑎᒃᑯᓐᓄᑦ. ᐱᓇᔭᖅᐸᑕ ᒐᕙᒪᑐᖃᒃᑯᓐᓄᑦ ᑮᓇᐅᔭᖃᖅᑎᑕᐅᔾᔪᑎᓂᒃ ᐊᖏᖅᑕᐅᓂᕐᒥᒃ, ᐃᒃᓯᓐᓇᖅᑕᐅᓯᒪᔪᖅ ᑭᓈᓗᖃᕐᕖᑦ ᖃᐅᔨᓴᖅᑕᐅᒃᑲᓐᓂᕋᔭᖅᑐᑦ ᓈᒻᒪᒍᑎᔪᑦ ᓴᓗᒻᒪᖅᓴᖅᑕᐅᓗᑎᒃ ᓄᑖᖑᕆᐊᖅᑕᐅᓗᑎᒃᓗ ᐱᓕᕆᐊᖃᕐᓗᓂ ᐃᓚᒋᐊᕐᓗᒍ ᒫᓐᓇ ᐊᒃᑕᕐᕕᖓᓂ.
ᐱᓕᕆᐊᖑᓯᒪᔪᑦ

## Slide 9
ᖃᐅᔨᓴᕈᑎᓕᕆᓂᖅ ᐱᓕᕆᐊᖅ
ᐃᓂᖓ | ᑭᓲᓂᖓ | ᐊᑯᓚᐃᓐᓂᖓ | ᐱᔭᐅᔪᒪᔪᖅ
ARV-1 | ᐃᒥᓪᓚᑦᑖᖃᕐᓂᖅ ᐊᒪᕈᖅ ᑰᖕᒥ ᓴᓗᒻᒪᖅᓴᖅᑕᐅᓚᐅᙱᑎᓪᓗᒍ. | ᑕᖅᑭᑕᒫᑦ | ᐊᓯᔾᔨᕐᓗᒍ ᐊᒪᕈᖅ ᑰᖓᓄᑦ
ARV-2a | ᑭᓈᓗᒃ ᑯᕕᔭᐅᓂᖓ ᑰᒻᒧᑦ ᐃᒫᓄᓪᓘᓐᓃᑦ ᑯᕕᑎᑕᐅᕝᕕᖕᒥ ᐊᒃᑕᑯᓄᑦ ᐃᒋᑦᑎᕕᒃ. | ᑕᖅᑭᑕᒫᑦ ᐊᑐᖅᑎᓪᓗᒍ ᑕᖅᑮᑦ ᒪᐃᒥ ᐋᒍᓯᒧᑦ ᑯᕕᑎᑕᐅᓚᐅᙱᑎᓪᓗᒍ ᐊᒃᑐᖅᑕᐅᓇᔭᖅᑐᓂ ᐃᒪᕐᒧᑦ. ᐅᓗᕆᐊᓇᕐᓂᖏ ᐊᑦᑕᕐᓇᖅᑐᓖᑦ ᐊᕐᕌᒍᑕᒫᑦ | ᐲᕐᓗᒍ ᐅᓗᕆᐊᓇᕈᓐᓇᖅᑐᓂ ᖃᐅᔨᓴᕐᓂᖅ
ARV-2b | ᑭᓈᓗᒃ ᑯᕕᔭᐅᓂᖓ ᑰᒻᒧᑦ ᐃᒫᓄᓪᓘᓐᓃᑦ ᐲᖅᓯᕕᖕᒥ ᓄᑖᖅ ᐊᒃᑕᕐᕕᒃ ᐊᒃᑕᖅᑕᐅᔪᕕᓂᕐᓄᑦ ᐃᓂᖓ. |  | ᐲᔭᕐᓗᒍ ᖃᐅᔨᒪᔪᒧᑦ ᓄᑖᖅ ᐊᒃᑕᕐᕕᖕᒥ
ARV-3 | ᑭᓈᓗᒃ ᓄᓇᓯᐅᑎᒥ ᓂᐅᕋᐃᕕᖕᒥ. | ᐊᑐᙱᑦᑐᖅ | ᐊᑐᓕᖅᑎᒃᑲᓐᓂᕐᓗᒍ ᐃᓚᓗᒍᓗ ᑭᓈᓗᒃ ᑯᕕᔭᐅᓂᖓ ᑰᒻᒧᑦ ᐃᒫᓄᓪᓘᓐᓃᑦ ᓂᐅᕋᖅᑕᑦ ᓄᑖᒧᑦ ᑭᓈᓗᖃᐅᑎᒧᑦ ᐃᒪᖅᓲᓂᕐᒧᓪᓗ
Station | Description | Frequency | Request
ARV-1 | Raw water supply at Wolf River prior to treatment. | Monthly | Change to Wolf Creek
ARV-2a | Effluent from the discharge point of the Solid Waste Disposal Facility. | Monthly during the months of May to August and prior to discharge of accumulated impacted water. Acute Toxicity Annually | Remove acute toxicity testing
ARV-2b | Effluent from the discharge point of the New Solid Waste Disposal Facility. |  | Remove the reference to a new solid waste facility
ARV-3 | Raw Sewage at truck offload point. | Not Active | Re-activate and add a point where effluent discharges from new lagoon to wetland
Sampling Program

## Slide 10
ᖃᐅᔨᓴᕈᑎᓕᕆᓂᖅ ᐱᓕᕆᐊᖅ
ᐃᓂᖓ | ᑭᓲᓂᖓ |  | ᐱᔭᐅᔪᒪᔪᖅ
ARV-4 | ᑭᓈᓗᒃ ᑯᕕᔭᐅᓂᖓ ᑰᒻᒧᑦ ᐃᒫᓄᓪᓘᓐᓃᑦ ᐲᖅᓯᕕᖕᒥ ᓴᓂᕐᓂᑦ ᐊᓂᑦᑎᓂᖅ ᑭᓱᓕᕆᕝᕕᒃ (ᐃᓱᐊᓂ ᐃᒪᖅᓱᒃ). | ᐱᐅᓂᕆᔭᖓ ᑕᖅᑭᑕᒫᑦ ᐊᑐᖅᑎᓪᓗᒍ ᑕᖅᑮᑦ ᒪᐃᒥ ᐊᐅᒍᔅᑎ. ᐅᓗᕆᐊᓇᕐᓂᖏ ᐊᑦᑕᕐᓇᖅᑐᓖᑦ ᐊᕐᕌᒍᑕᒫᑦ | ᐲᕐᓗᒍ ᐅᓗᕆᐊᓇᕈᓐᓇᖅᑐᓂ ᖃᐅᔨᓴᕐᓂᖅ
ARV-5 | ᐲᔭᐅᓗᓂ ᓴᕕᕋᔭᖃᕐᕕᒃ ᐊᑐᕈᓐᓃᖅᑐᓂᒃ ᐃᓂᒋᔭᖓᓂ. | ᑕᖅᑭᑕᒫᑦ ᐊᑐᖅᑎᓪᓗᒍ ᖃᐅᔨᔭᐅᓇᓱᒃᓇᓂ ᑯᕕᔪᓂ. | ᐊᑐᙱᑦᑐᖅ
ARV-6 | ᐲᔭᐅᓗᓂ ᐅᓗᕆᐊᓇᖅᑐᓂᑦ ᐊᒃᑕᑯᑦ ᓱᓇᒃᑯᑖᖃᕐᕕᖕᒥ. |  | 
ARV-7 | ᐃᒪᖅ ᐃᑎᓂᖓ ᐊᒪᕈᖅ ᑰᖕᒥ. | ᑕᖅᑭᑕᒫᑦ ᐊᑐᖅᑎᓪᓗᒍ ᐃᒪᖅ ᐊᐅᒃᓯᒪᓕᕌᖓᑦ. | ᐲᕐᓗᒍ ᐱᖁᑎᖃᕐᕕᒃᑲᓐᓂᖅ
Station | Description |  | Request
ARV-4 | Effluent from the discharge point of the Sewage Disposal Facility (end of Wetland). | Quality Monthly during the months of May to August. Acute Toxicity Annually | Remove acute toxicity testing
ARV-5 | Discharge from the Bulky Metal Waste Area. | Monthly during periods of observed flow. | N/A
ARV-6 | Discharge from the Hazardous Waste Storage Area. |  | 
ARV-7 | Water level in Wolf River. | Monthly during periods of open water. | Remove resupply
Sampling Program

## Slide 11
ᖃᐅᔨᓴᕈᑎᓕᕆᓂᖅ ᐱᓕᕆᐊᖅ
ᐃᓂᖓ | ᑭᓲᓂᖓ |  | ᐱᔭᐅᔪᒪᔪᖅ
ARV-8 | ᐃᒪᖅ ᐃᑎᓂᖓ ᑭᓈᓗᖕᓄᑦ ᐊᒃᑕᖅᑕᐅᔪᕕᓂᕐᓄᑦ ᐃᓂᖓ ᑭᓈᓗᖃᕐᕕᒃ. | ᑕᖅᑭᑕᒫᑦ ᐊᑐᖅᑎᓪᓗᒍ ᒪᙳᒃᓯᒪᔪᑦ ᖃᓄᐃᓕᖓᓂᖏᑦ. | ᐲᕐᓗᒍᑦ
ARV-9 | ᓱᕈᕐᓇᖅᑑᑉ ᑰᒍᔾᔭᐅᓂᖓ ᐊᑦᑕᕐᕕᒻᒥᑦ | ᑕᖅᑭᑕᒫᑦ | ᐊᑐᙱᑦᑐᖅ
ARV-10 | ᑭᓈᓗᒃ ᑯᕕᔭᐅᓂᖓ ᑰᒻᒧᑦ ᐃᒫᓄᓪᓘᓐᓃᑦ ᐲᖅᓯᕕᖕᒥ ᐅᖅᓱᐊᓗᒃᓴᒥ ᓱᕈᖅᓯᒪᔪᓂ ᐃᔾᔪᒃᑯᕕᒃ ᐃᓅᓕᓴᕐᑕᐅᓃᑦ ᐱᓕᕆᕕᒃ | ᓇᓗᓇᐃᕐᑕᐅᓛᖅᑐᖅ ᑎᑎᕋᖅᓯᒪᔪᑦ ᐃᓚᖓ D, ᐱᖁᑎ 10 | ᐲᕐᓗᒍᑦ
ARV-11 | ᑭᓈᓗᒃ ᑯᕕᔭᐅᓂᖓ ᑰᒻᒧᑦ ᐃᒫᓄᓪᓘᓐᓃᑦ ᐃᒻᒥᒃᑲᓐᓂᖁᓇᒍ ᓱᕈᖅᓯᒪᔪᒥ ᐃᔾᔪᓂᑦ ᐊᕙᑎᖏᓐᓂ. | ᓇᓗᓇᐃᕐᑕᐅᓛᖅᑐᖅ ᑎᑎᕋᖅᓯᒪᔪᑦ ᐃᓚᖓ D, ᐱᖁᑎ 14 (c) | ᐲᕐᓗᒍᑦ
Station | Description |  | Request
ARV-8 | Water level in Sewage Disposal Facility lagoon. | Monthly during Thawed conditions. | Remove
ARV-9 | Run-off from Solid Waste Disposal Facility | Monthly | N/A
ARV-10 | Effluent from the Final Discharge Point of the Hydrocarbon Impacted Soil Storage and Treatment Facility | To be determined in accordance with Part D, Item 10 | Remove
ARV-11 | Effluent discharge from dewatering contaminated soil areas. | To be determined in accordance with Part D, Item 14 (c) | Remove
Sampling Program

## Slide 12
ᒪᓕᒋᐊᓕᓐᓂᑦ ᕿᒥᕐᕈᓂᖅ
Regulatory Review

## Slide 13: ᐊᕙᑎᓕᕆᓂᕐᒧᑦ ᐊᒻᒪ ᓯᓚᐅᑉ ᐊᓯᔾᔨᖅᐸᓪᓕᐊᓂᖓᓄᑦ ᑲᓇᑕᒥᑦ ᐅᖃᐅᓯᐅᔪᑦ
01. Monitoring Program Compliance Point ARV-4
CGS Response:
ARV-4 will be established downstream in the wetland treatment area accessible by municipal staff.
01. ᖃᐅᔨᓴᐃᓐᓇᕐᓂᖅ ᐱᓕᕆᐊᒃᓴᒧᑦ ᒪᓕᑦᑎᐊᕐᓂᕐᒥᒃ ARV-4
ᓄᓇᓕᖕᓂ ᒐᕙᒪᒃᑯᓐᓂᓗ ᐱᔨᑦᑎᕋᖅᑎᒃᑯᑦ ᑭᐅᔾᔪᑎᖓ:
ARV-4 ᐋᖅᑭᒃᑕᐅᓗᓂ ᐊᑐᓕᖁᔭᐅᔪᒧᑦ ᐃᓂᒧᑦ ᐃᖏᕐᕋᓗᓂ ᐃᒪᖅᓱᕐᒧᑦ ᐊᕙᑎᖓᓄᑦ ᐅᐸᒃᑕᐅᔪᓐᓇᖅᑐᒧᑦ Hᐋᒻᒪᓚᒃᑯᑦ ᐃᖅᑲᓇᐃᔭᖅᑎᖏᓐᓄᑦ.
ECCC Comments

## Slide 14: ᐊᕙᑎᓕᕆᓂᕐᒧᑦ ᐊᒻᒪ ᓯᓚᐅᑉ ᐊᓯᔾᔨᖅᐸᓪᓕᐊᓂᖓᓄᑦ ᑲᓇᑕᒥᑦ ᐅᖃᐅᓯᐅᔪᑦ
02. Project Timelines
CGS Response:
CGS will provide an updated timeline for the wastewater and solid waste projects.
02. ᐱᓕᕆᐊᒃᓴᒧᑦ ᖃᖓᒃᑰᕈᑎᒃᓴᖏᑦ
ᓄᓇᓕᖕᓂ ᒐᕙᒪᒃᑯᓐᓂᓗ ᐱᔨᑦᑎᕋᖅᑎᒃᑯᑦ ᑭᐅᔾᔪᑎᖓ:
ᓄᓇᓕᖕᓂ ᒐᕙᒪᒃᑯᓐᓂᓗ ᐱᔨᑦᑎᕋᖅᑎᒃᑯᑦ ᐱᑎᑦᑎᓇᔭᖅᑐᑦ ᓄᑖᖑᕆᐊᖅᓯᒪᔪᒥᒃ ᖃᖓᒃᑰᓇᔭᖅᑐᓂ ᐃᒪᑦᑎᐊᕙᐅᙱᑦᑐᓄᑦ ᐊᒃᑕᑯᓄᓪᓗ ᐱᓕᕆᐊᒃᓴᓄᑦ.
ECCC Comments

## Slide 15: ᐊᕙᑎᓕᕆᓂᕐᒧᑦ ᐊᒻᒪ ᓯᓚᐅᑉ ᐊᓯᔾᔨᖅᐸᓪᓕᐊᓂᖓᓄᑦ ᑲᓇᑕᒥᑦ ᐅᖃᐅᓯᐅᔪᑦ
03. Abandonment and Restoration Plans
CGS Response:
There is no plan to close the solid waste disposal area or the bulky metals area. The business case recommended that both areas remain in use indefinitely, and expansion take place.
An investigation of the abandoned lagoon cells to assess their potential to be remediated and re-used to expand the current solid waste will be included in the next phase of the solid waste project.
03. ᑲᒪᒋᔭᐅᔾᔮᕈᓐᓃᖅᑐᓄᑦ ᐅᑎᖅᑎᑎᓂᕐᒧᓪᓗ ᐸᕐᓇᐅᑎᑦ
ᓄᓇᓕᖕᓂ ᒐᕙᒪᒃᑯᓐᓂᓗ ᐱᔨᑦᑎᕋᖅᑎᒃᑯᑦ ᑭᐅᔾᔪᑎᖓ:
ᐸᕐᓇᐅᑎᑕᖃᙱᑦᑐᖅ ᒪᑐᑎᓪᓗᒍ ᐊᒃᑕᕐᕕᒃ ᐊᕙᑎᖓ ᓄᑕᐅᙱᑦᑐᓪᓘᓐᓃᑦ ᓴᕕᕋᔭᖃᕐᕕᖕᒥ. ᐱᓕᕆᐊᒃᓴᕆᔭᐅᔪᖅ ᐱᖁᔨᓪᓗᓂ ᑕᒪᒃᑮ ᐊᕙᑎᖏᑦ ᐊᑐᖅᑕᐅᙱᓐᓇᕐᓗᑎᒃ, ᐊᖏᒃᓕᒋᐊᖅᑎᑦᑎᓂᕐᓗ ᐊᑐᕐᓗᓂ.
ᖃᐅᔨᓴᕐᓂᖅ ᖓᑐᖅᑕᐅᔪᓐᓃᖅᑐᒥᒃ ᑭᓈᓗᖃᕐᕕᖕᒥ ᖃᐅᔨᓴᕐᓗᒍ ᐊᑐᒃᑲᓐᓂᕈᓐᓇᕐᒪᖔᑦ ᐋᖅᑭᒋᐊᖅᑕᐅᓗᓂ ᐊᑐᖅᑕᐅᒃᑲᓐᓂᓕᕐᓗᓂᓗ ᐊᖏᒃᓕᒋᐊᕐᓗᒍ ᒫᓐᓇ ᑭᓈᓗᖃᕐᕕᒃ ᐃᓚᐅᑎᑕᐅᓂᐊᖅᑐᖅ ᑭᖑᓪᓕᕐᒥ ᐊᑐᓕᖅᐸᑦ ᑭᓈᓗᖃᕐᕕᖕᒧᑦ ᐱᓕᕆᐊᖅ.
ECCC Comments

## Slide 16: ᐊᕙᑎᓕᕆᓂᕐᒧᑦ ᐊᒻᒪ ᓯᓚᐅᑉ ᐊᓯᔾᔨᖅᐸᓪᓕᐊᓂᖓᓄᑦ ᑲᓇᑕᒥᑦ ᐅᖃᐅᓯᐅᔪᑦ
04. Lagoon Desludging
CGS Response:
It was determined that since the lagoon cell is expected to be decommissioned, desludged, remediated, and upgraded in 2024, desludging in 2021 would provide minimal benefit compared to the labor required for the undertaking.
A new OM plan containing a sludge management plan that includes assessment and disposal techniques, as well as a disposal location, will be prepared by the design consultant and contractor for the new 2-cell lagoon.
04. ᑭᓈᓗᖃᕐᕕᖕᒥ ᐃᕐᕈᖅᑐᐃᓂᖅ
ᓄᓇᓕᖕᓂ ᒐᕙᒪᒃᑯᓐᓂᓗ ᐱᔨᑦᑎᕋᖅᑎᒃᑯᑦ ᑭᐅᔾᔪᑎᖓ:
ᐱᔭᐅᔪᒪᓚᐅᖅᑐᖅ ᑭᓈᓗᖃᕐᕕᒃ ᓂᕆᐅᒋᔭᐅᓂᖓᓄᑦ ᐃᕐᕈᖅᑐᖅᑕᐅᒃᑲᓐᓂᕐᓂᐊᕐᓂᕐᒧᑦ, ᐋᖅᑭᒋᐊᖅᑕᐅᓂᕐᒧᑦ ᓄᑖᖑᕆᐊᖅᑕᐅᓂᕐᒧᓪᓗ 2024−ᒥ, ᐃᕐᕈᖅᑐᖅᑕᐅᓪᓗᓂ 2021−ᒥ ᐱᑎᑦᑎᓇᔭᖅᑐᖅ ᐱᕚᓪᓕᕈᑎᐊᕐᔪᖕᒥᒃ ᐊᔾᔨᒋᙱᓪᓗᓂᐅᒃ ᓴᓇᔨᖃᕆᐊᖃᕐᓂᖓ ᐱᓕᕆᐊᖃᕐᓂᕐᒧᑦ.
ᓄᑖᖅ ᐊᐅᓚᔾᔪᑏᑦ ᐋᖅᑭᐅᒪᔾᔪᑎᓪᓗ ᐸᕐᓇᐅᑎ ᐃᓗᓕᖃᕐᖢᓂ ᐃᒪᖅᓱᕐᓄᑦ ᐊᐅᓚᑦᑎᓂᕐᒥᒃ ᐸᕐᓇᐅᑎ ᐃᓚᐅᑎᑦᑎᓪᓗᓂ ᖃᐅᔨᓴᕈᑎᒃᓴᓂᑦ ᐃᒋᑦᑎᓂᕐᒧᓪᓗ ᐊᑐᕈᓯᕐᓂᒃ, ᐊᒻᒪᓗᑦᑕᐅᖅ ᐃᒋᑦᑎᓂᕐᒧᑦ ᐃᓂᖓᓂᒃ, ᐸᕐᓇᒃᑕᐅᓂᐊᖅᑐᖅ ᐋᖅᑭᒃᓯᒪᓂᒃᓴᖓᓄᑦ ᖃᐅᔨᒃᑲᐃᔨᒧᑦ ᐊᒻᒪ ᐊᖏᖃᑎᒌᓂᕐᒧᑦ ᐱᓕᕆᑎᑕᐅᔪᒃᓴᒧᑦ ᓄᑖᒧᑦ ᒪᕐᕈᐃᓕᖓᓪᓗᓂ ᑭᓈᓗᖃᕐᕕᖕᓄᑦ.
ECCC Comments

## Slide 17: ᐊᕙᑎᓕᕆᓂᕐᒧᑦ ᐊᒻᒪ ᓯᓚᐅᑉ ᐊᓯᔾᔨᖅᐸᓪᓕᐊᓂᖓᓄᑦ ᑲᓇᑕᒥᑦ ᐅᖃᐅᓯᐅᔪᑦ
05. Additional Monitoring Stations
CGS Response:
The licensee agrees that a monitoring station at the point of discharge from the lagoon should be included in the new license.
However, this station should not be considered a compliance point and no effluent limits should be imposed at this point since it represents only partially treated effluent.
05. ᖃᐅᔨᓴᕈᑎᒃᑲᓐᓂᐅᔪᓐᓇᕐᑐᑦ ᐃᓂᖃᕐᕕᖏᑦ
ᓄᓇᓕᖕᓂ ᒐᕙᒪᒃᑯᓐᓂᓗ ᐱᔨᑦᑎᕋᖅᑎᒃᑯᑦ ᑭᐅᔾᔪᑎᖓ:
ᐱᔪᓐᓇᐅᑎᑖᖅᓯᒪᔪᖅ ᐊᖏᖃᑎᖃᖅᐳᖅ ᖃᐅᔨᓴᐃᓐᓇᕐᕕᒃ ᖁᕕᑎᑦᑎᕕᐅᓂᐊᖅᑐᒥ ᑭᓈᓗᖃᕐᕕᖕᒥ ᐃᓚᐅᑎᑕᐅᓪᓗᐊᖅᑐᖅ ᓄᑖᒧᑦ ᐱᔪᓐᓇᐅᑎᒧᑦ.
ᑕᐃᒪᐃᒃᑲᓗᐊᖅᑎᓪᓗᒍ, ᑖᓐᓇ ᐃᓂᐅᓂᐊᖅᑐᖅ ᐃᓱᒪᒋᔭᐅᔭᕆᐊᖃᙱᑦᑐᖅ ᒪᓕᑦᑎᐊᕐᕕᐅᖕᒪᖔᑦ ᐃᓱᖃᕐᕕᖃᕐᓂᖓᓗ ᐊᑐᖅᑕᐅᔭᕆᐊᖃᙱᑦᑐᖅ ᒫᓐᓇᐅᔪᖅ ᑭᒡᒐᖅᑐᐃᓂᖓᓄᑦ ᐃᓚᐅᓐᓇᖓᓂ ᐋᖅᑭᒋᐊᖅᓯᒪᔪᒥ ᑭᓈᓗᖃᕐᕕᖕᒥ.
ECCC Comments

## Slide 18: ᐊᕙᑎᓕᕆᓂᕐᒧᑦ ᐊᒻᒪ ᓯᓚᐅᑉ ᐊᓯᔾᔨᖅᐸᓪᓕᐊᓂᖓᓄᑦ ᑲᓇᑕᒥᑦ ᐅᖃᐅᓯᐅᔪᑦ
06. Duplicate Sampling
CGS Response:
The QA/QC Plan was updated to include information on the frequency of replicate/duplicate samples in the sampling program.
06. ᖃᐅᔨᓴᕈᑎᓕᕆᓂᖅ
ᓄᓇᓕᖕᓂ ᒐᕙᒪᒃᑯᓐᓂᓗ ᐱᔨᑦᑎᕋᖅᑎᒃᑯᑦ ᑭᐅᔾᔪᑎᖓ:
ᐱᐅᓂᖓ ᖃᐅᔨᒪᓗᒍ/ᐱᐅᓂᖓ ᐊᐅᓚᓪᓗᒍ ᐸᕐᓇᐅᑎ ᓄᑖᖑᕆᐊᖅᑕᐅᓂᐊᖅᑐᖅ ᐃᓚᐅᑎᑦᑎᓗᑎᒃ ᓇᓗᓇᐃᔭᐅᑎᓂᒃ ᐊᑐᒐᔪᖕᓂᖓᒍᑦ ᐱᐅᕋᕐᓗᑎᒃ/ᐲᔭᐃᓗᑎᒃ ᖃᐅᔨᓴᒐᒃᓴᓂᒃ ᖃᐅᔨᓴᕐᓂᕐᒧᑦ ᐱᓕᕆᐊᒃᓴᒥ.
ECCC Comments

## Slide 19: ᑯᐄᓐ ᑭᒡᒐᖅᑐᖅᑎᖓ−ᓄᓇᖃᖅᑳᖅᓯᒪᔪᓕᕆᓂᖅ ᐊᒻᒪ ᐃᓄᓕᕆᔨᑐᖃᒃᑯᑦ ᑲᓇᑕᒥ ᐅᖃᐅᓯᐅᔪᑦ
01. Solid Waste Site Capacity
CGS Response:
Beginning in 2017, the Municipality began shredding depolluted metal waste to increase capacity at the site. The metal was then used as cover material for the landfill which resulted in compaction that drastically increased the capacity.
CGS will undertake a study in 2022/23 to determine how to further improve capacity of the current solid waste site and evaluate the feasibility of expanding into the abandoned lagoon cells after proper remediation.
01. ᐊᑕᕐᕕᐅᑉ ᐃᓂᒋᔭᐅᔪᓇᕐᓂᖓ
ᓄᓇᓕᖕᓂ ᒐᕙᒪᒃᑯᓐᓂᓗ ᐱᔨᑦᑎᕋᖅᑎᒃᑯᑦ ᑭᐅᔾᔪᑎᖓ:
ᐱᒋᐊᕐᖢᓂ 2017-ᒥ, Hᐋᒻᒪᓚᒃᑯᑦ ᓱᕋᒃᑎᕆᕙᓪᓕᐊᕙᓕᕐᖢᑎᒃ ᓱᕈᖅᓯᒪᔪᓂᒃ ᓴᕕᕋᔭᖕᓂᑦ ᐃᓂᖃᓕᒃᑲᓐᓂᖁᓪᓗᒍ. ᓴᕕᕋᔭᐃᑦ ᐊᑐᖅᑕᐅᓕᕆᓪᓗᑎᒃ ᕐᑳᕆᓪᓗᓂᒋᑦ ᐊᒃᑕᕐᕕᖕᒥ ᐱᑎᑦᑎᓪᓗᓂ ᐱᖁᑎᖃᕐᕕᐅᓪᓗᓂ ᐃᓂᖃᓕᖅᑎᑦᑎᒃᑲᓐᓂᕐᔪᐊᖅᑐᒥᒃ.
ᓄᓇᓕᖕᓂ ᒐᕙᒪᒃᑯᓐᓂᓗ ᐱᔨᑦᑎᕋᖅᑎᒃᑯᑦ ᐱᓕᕆᐊᖃᕋᔭᖅᑐᑦ ᖃᐅᔨᓴᕈᑎᒃᓴᓂᒃ 2022/23 ᖃᐅᔨᓇᓱᒃᓗᑎᒃ ᖃᓄᖅ ᐱᐅᓯᒋᐊᒃᑲᓐᓂᕈᓐᓇᕐᒪᖔᑦ ᐊᖏᓂᖓ ᒫᓐᓇ ᐊᒃᑕᕐᕕᒃ ᐃᓂᖓ ᖃᐅᔨᓴᕐᓗᒍᓗ ᑲᔪᓯᔪᓐᓇᑦᑎᐊᕐᒪᖔᑦ ᐊᖏᒃᓕᒋᐊᕐᓗᒍ ᐊᑐᖅᑕᐅᔪᓐᓃᖅᑐᒧᑦ ᑭᓈᓗᖃᕐᕕᖕᒧᑦ ᓈᒻᒪᒃᑐᒃᑯᑦ ᐋᖅᑭᒋᐊᖅᑕᐅᓚᐅᖅᑎᓪᓗᒍ.
CIRNAC Comments

## Slide 20: ᑯᐄᓐ ᑭᒡᒐᖅᑐᖅᑎᖓ−ᓄᓇᖃᖅᑳᖅᓯᒪᔪᓕᕆᓂᖅ ᐊᒻᒪ ᐃᓄᓕᕆᔨᑐᖃᒃᑯᑦ ᑲᓇᑕᒥ ᐅᖃᐅᓯᐅᔪᑦ
02. Lagoon Design Parameters
CGS Response:
Lagoon-wetland systems do not function to achieve treatment goals prior to discharging into the wetland. The wetland treatment area is a significant component of the treatment facility. The 2-cell lagoon system will be sized to retain wastewater for 12 months for a 20-year design life
Effluent will be decanted into the wetland treatment area in late summer once the wetland has had the opportunity to develop and runoff has passed through. Currently the effluent is benefiting from dilution rather than treatment, potentially resulting in lower effluent concentrations, but in reality, not better-quality effluent.
The pumping rate will be determined during design to optimize both drawn down time and effectiveness off the wetland treatment but it will be below the recommended maximum of 2500 m3/day to preserve the health of the marine receiving environment.
02. ᑭᓈᓗᖃᕐᕕᐅᑉ ᑕᐅᑦᑐᒃᓴᖓᑕ ᖃᐅᔨᓴᕈᑎᑦ
ᓄᓇᓕᖕᓂ ᒐᕙᒪᒃᑯᓐᓂᓗ ᐱᔨᑦᑎᕋᖅᑎᒃᑯᑦ ᑭᐅᔾᔪᑎᖓ:
ᑭᓈᓗᖃᕐᕕᖕᒥ ᐃᒪᖅᓱᓄᑦ ᐊᑐᖃᑦᑕᖅᑐᑦ ᐊᐅᓚᓂᖃᑦᑎᐊᙱᒻᒪᑕ ᐋᖅᑭᐊᓂᒃᓗᒋᑦ ᑐᕌᕆᔭᖏᑦ ᑯᕕᑎᑦᑎᓚᐅᙱᓐᓂᖏᓐᓂ ᐃᒪᖅᓱᕐᒧᑦ. ᐃᒪᖅᓱᕐᒥᑦ ᐋᖅᑭᒃᓱᐃᓂᖅ ᐊᕙᑎᖓ ᐱᔭᕆᐊᖃᓪᓚᕆᒃᑐᖅ ᐃᓗᓕᖓᓂ ᐋᖅᑭᒃᓱᐃᕕᒃ. ᒪᕐᕈᐃᓕᖓᔪᖅ ᑭᓈᓗᖃᕐᕕᒃ ᐊᑐᖃᑦᑕᖅᑐᒥ ᐊᖏᓂᖃᖅᑎᑕᐅᓂᐊᖅᑐᖅ ᐱᓯᒪᔪᓐᓇᕐᓗᒍ ᐃᒥᑦᑎᐊᕙᐅᙱᑦᑐᖅ ᑕᖅᑭᓄᑦ 12-ᓄᑦ ᐊᕐᕌᒍᓄᑦ 20-ᓄᑦ ᐊᑐᐃᓐᓇᕈᓐᓇᕐᓗᓂ.
ᑭᓈᓗᒃ ᑯᕕᔭᐅᓂᖓ ᑰᒻᒧᑦ ᐃᒫᓄᓪᓘᓐᓃᑦ ᑯᕕᔭᐅᓗᓂ ᐃᒪᖅᓱᕐᒧᑦ ᐋᖅᑭᒋᐊᖅᑕᒧᑦ ᐊᐅᔭᐅᑐᖃᓚᐅᖅᑎᓪᓗᒍ ᐃᒪᖅᓱᖅ ᐱᕕᖃᓚᐅᖅᑎᓪᓗᒍ ᐋᖅᑭᒃᓗᓂ ᑰᕌᓂᓚᐅᖅᑎᓪᓗᒍᓗ. ᒫᓐᓇᓕ ᑭᓈᓗᒃ ᑯᕕᔭᐅᓂᖓ ᑰᒻᒧᑦ ᐃᒫᓄᓪᓘᓐᓃᑦ ᐱᕚᓪᓕᖅᑎᑦᑎᔪᖅ ᓴᙲᒃᓕᒋᐊᕈᑎᓂᑦ ᒪᒥᓴᐃᓂᕐᒨᙱᑦᑐᖅ, ᐱᑎᑦᑎᓗᓂᐅᔪᒃᓴᐅᔪᖅ ᐊᑦᑎᖕᓂᖅᓴᒥ ᑭᓈᓗᒃ ᑯᕕᔭᐅᓂᖓ ᑰᒻᒧᑦ ᐃᒫᓄᓪᓘᓐᓃᑦ ᐱᓕᕆᐊᖑᔪᓂᑦ, ᑭᓯᐊᓂ ᐱᓪᓚᑦᑖᖅᑐᒥ, ᐱᐅᓂᖅᓴᐅᓗᓂᐅᙱᑦᑐᖅ ᑭᓈᓗᒃ ᑯᕕᔭᐅᓂᖓ ᑰᒻᒧᑦ ᐃᒫᓄᓪᓘᓐᓃᑦ.
ᒥᓪᓗᐊᖅᑕᐅᓂᖓᓄᑦ ᖃᓄᑎᒋᐅᓂᖓ ᖃᐅᔨᔭᐅᓂᐊᖅᑐᖅ ᐋᖅᑭᒃᓯᒪᓂᖓᒎᓕᖅᐸᑦ ᐱᐅᓯᒋᐊᖁᓪᓗᒋᑦ ᑕᒪᒃᑮ ᑯᕕᑎᑕᐅᔭᕆᐊᖃᓕᕌᖓᑦ ᐊᑑᑎᖃᑦᑎᐊᕐᓂᖓᓗ ᐃᒪᖅᓱᒃ ᐋᖅᑭᒋᐊᖅᑕᐅᑎᓪᓗᒍ, ᑭᓯᐊᓂ ᑐᖔᓃᓐᓂᐊᖅᑐᖅ ᐱᖁᔭᐅᔫᑉ ᐊᖏᓛᖓᓂ 2500 m3/ᐅᓪᓗᕐᒧᑦ ᐱᓗᐊᖅᑕᐅᓕᓗᒍ ᐋᓐᓂᐊᖃᖅᑕᐃᓕᒪᓂᖅ ᐃᒪᕐᒥᐅᑕᓄᑦ ᐱᔪᓂᒃ ᐊᕙᑎᒥᒃ.
CIRNAC Comments

## Slide 21: ᑯᐄᓐ ᑭᒡᒐᖅᑐᖅᑎᖓ−ᓄᓇᖃᖅᑳᖅᓯᒪᔪᓕᕆᓂᖅ ᐊᒻᒪ ᐃᓄᓕᕆᔨᑐᖃᒃᑯᑦ ᑲᓇᑕᒥ ᐅᖃᐅᓯᐅᔪᑦ
03. Lagoon Effluent Parameters
CGS Response:
The licensee is requesting that the effluent parameter limits at the end of the wastewater treatment facility be changed to cBOD/TSS of 100/120 mg/L. This error in the OM Plan was fixed in the newer version.
03. ᑭᓈᓗᖃᕐᕕᒃ ᑭᓈᓗᒃ ᑯᕕᔭᐅᓂᖓ ᑰᒻᒧᑦ ᐃᒫᓄᓪᓘᓐᓃᑦ ᖃᐅᔨᓴᕈᑎᑦ
ᓄᓇᓕᖕᓂ ᒐᕙᒪᒃᑯᓐᓂᓗ ᐱᔨᑦᑎᕋᖅᑎᒃᑯᑦ ᑭᐅᔾᔪᑎᖓ:
ᐱᔪᓐᓇᐅᑎᑖᖅᓯᒪᔪᖅ ᑐᒃᓯᕋᖅᑐᖅ ᑭᓈᓗᒃ ᑯᕕᔭᐅᓂᖓ ᑰᒻᒧᑦ ᐃᒫᓄᓪᓘᓐᓃᑦ ᖃᐅᔨᓴᕈᑎᑦ ᐃᓱᖃᖅᑎᑦᑎᓗᓂ ᐃᓱᐊᓂ ᐃᒪᑦᑎᐊᕙᐅᙱᑦᑐᖅ ᐋᖅᑭᒃᓱᕐᕕᖓᓂ ᐊᓯᔾᔨᖅᑕᐅᓗᓂ cBOD/TSS ᐅᕗᖓ 100/120 mg/L. ᑖᓐᓇ ᑕᒻᒪᖅᓯᒪᔪᖅ ᐊᐅᓚᔾᔪᑏᑦ ᐋᖅᑭᐅᒪᔾᔪᑎᓪᓗ ᐸᕐᓇᐅᑎ ᐋᖅᑭᒃᑕᐅᓂᐊᖅᑐᖅ ᓄᑖᖑᓂᖅᓴᒧᑦ.
CIRNAC Comments

## Slide 22: ᑯᐄᓐ ᑭᒡᒐᖅᑐᖅᑎᖓ−ᓄᓇᖃᖅᑳᖅᓯᒪᔪᓕᕆᓂᖅ ᐊᒻᒪ ᐃᓄᓕᕆᔨᑐᖃᒃᑯᑦ ᑲᓇᑕᒥ ᐅᖃᐅᓯᐅᔪᑦ
04. Lagoon Liner
CGS Response:
In the event that the liner is damaged resulting in a leak, the effluent will passively exfiltrate into the wetland treatment area, which is downgrade from the lagoon, in the same way that it does with the current permeable lagoon.
The new lagoon will use the same wetland as the current lagoon therefore no additional land will be contaminated.
In addition, the effluent samples taken, and lagoon water levels will be monitored in order to detect evidence of a leak. Repairs to the liner will be completed if there is a leak.
04. ᑭᓈᓗᖃᕐᕕᒃ ᐃᑭᐊᕐᒥᖓ
ᓄᓇᓕᖕᓂ ᒐᕙᒪᒃᑯᓐᓂᓗ ᐱᔨᑦᑎᕋᖅᑎᒃᑯᑦ ᑭᐅᔾᔪᑎᖓ:
ᐊᑐᕋᔭᖅᐸᑦ ᐃᑭᐊᕐᒥᖓ ᓱᕋᒃᓗᓂ ᑯᑐᒃᑎᑦᑎᓗᓂ, ᑭᓈᓗᒃ ᑯᕕᔭᐅᓂᖓ ᑰᒻᒧᑦ ᐃᒫᓄᓪᓘᓐᓃᑦ ᐊᖅᑯᑎᖓᒍᑦ ᓅᑉᐸᓪᓕᐊᖏᓐᓇᕐᓂᐊᖅᑐᖅ ᐃᒪᖅᓱᖅ ᐋᖅᑭᒋᐊᖅᑕᐅᓯᒪᔪᒧᑦ, ᐊᑦᑎᖕᓂᖅᓴᐅᑎᑦᑎᔪᖅ ᖃᓄᐃᓕᖓᓂᖓᓂᒃ ᑭᓈᓗᖃᕐᕕᖕᒥ, ᑕᐃᒪᓐᓇᑎᒋ ᐱᖃᑦᑕᖅᑕᖓᑐᑦ ᒫᓐᓇ ᐱᕕᖃᖅᑎᑦᑎᔪᒥᒃ ᑭᓈᓗᖃᕐᕕᖕᒥ.
ᓄᑖᖅ ᑭᓈᓗᖃᕐᕕᒃ ᐊᑐᕐᓂᐊᖅᑐᖅ ᑖᓐᓇᑦᑕᐃᓐᓇᖅ ᐃᒪᖅᓱᕐᒥᒃ ᒫᓐᓇ ᑭᓈᓗᖃᕐᕕᖕᒥ ᑕᐃᒪᐃᒻᒪᑦ ᓄᓇᒃᑲᓐᓂᕐᒥᒃ ᓱᕈᖅᑐᖃᔾᔮᙱᒻᒪᑦ.
ᐃᓚᒃᑲᓐᓂᖓ, ᑭᓈᓗᒃ ᑯᕕᔭᐅᓂᖓ ᑰᒻᒧᑦ ᐃᒫᓄᓪᓘᓐᓃᑦ ᖃᐅᔨᓴᕈᑎᒃᓴᑦᐱᔭᐅᒃᐸᑕ, ᑭᓈᓗᖃᕐᕕᒃᓗ ᐃᒪᖓ ᖃᓄᑎᒋᐅᓂᖏᑦ ᖃᐅᔨᓴᖅᑕᐅᖏᓐᓇᕋᔭᖅᑐᑦ ᖃᐅᔨᔪᓐᓇᕐᓗᑎᒃ ᑯᑐᒃᑐᒥᒃ. ᐋᖅᑭᒋᐊᕈᑎᑦ ᐃᑭᐊᕐᒥᖓᓄᑦ ᐱᔭᕇᖅᑕᐅᓇᔭᖅᑐᑦ ᑯᑐᒃᑐᖃᕋᔭᖅᐸᑦ.
CIRNAC Comments

## Slide 23: ᑯᐄᓐ ᑭᒡᒐᖅᑐᖅᑎᖓ−ᓄᓇᖃᖅᑳᖅᓯᒪᔪᓕᕆᓂᖅ ᐊᒻᒪ ᐃᓄᓕᕆᔨᑐᖃᒃᑯᑦ ᑲᓇᑕᒥ ᐅᖃᐅᓯᐅᔪᑦ
05. Removal of Inactive Monitoring Stations
CGS Response:
A “hydrocarbon impacted storage facility” was never constructed and does not exist therefore ARV-10 and ARV-11 do not exist.
Having inactive compliance points listed in the monitoring station program table is unnecessarily cumbersome for operational staff and provide no benefit.
05. ᐲᔭᐃᓂᖅ ᐊᑐᙱᑦᑐᓂᒃ ᖃᐅᔨᓴᐃᓐᓇᕐᕕᖕᓂᑦ
ᓄᓇᓕᖕᓂ ᒐᕙᒪᒃᑯᓐᓂᓗ ᐱᔨᑦᑎᕋᖅᑎᒃᑯᑦ ᑭᐅᔾᔪᑎᖓ:
“ᐅᖅᓱᐊᓗᒃᓴᕐᒧᑦ ᐊᒃᑐᖅᑕᐅᔪᓄᑦ ᑐᖅᑯᖅᓯᕝᕕᒃ” ᓴᓇᔭᐅᓚᐅᖅᓯᒪᙱᑦᑐᖅ ᐱᑕᖃᙱᖦᖢᓂᓗ ᑕᐃᒪᐃᒻᒪᑦ ARV-10 ᐊᒻᒪ ARV-11 ᐱᑕᖃᙱᑦᑑᒃ.
ᐊᑐᙱᑦᑐᓂᒃ ᒪᓕᑦᑎᐊᕈᑎᒃᓴᓂᒃ ᑎᑎᕋᖅᓯᒪᔪᓂᒃ ᖃᐅᔨᓴᐃᓐᓇᕐᕕᖕᒥ ᐱᓕᕆᐊᒃᓴᓄᑦ ᐱᔭᕆᐊᖃᙱᑦᑐᒥᒃ ᐊᔪᕐᓇᖅᑐᖅᓯᐅᕈᑎᐅᕗᖅ ᐊᐅᓚᓂᖏᓐᓄᑦ ᐃᖅᑲᓇᐃᔭᖅᑎᓄᑦ ᐱᕚᓪᓕᖅᑎᑦᑎᙱᖦᓗᑎᒃᓗ.
CIRNAC Comments

## Slide 24: ᑯᐄᓐ ᑭᒡᒐᖅᑐᖅᑎᖓ−ᓄᓇᖃᖅᑳᖅᓯᒪᔪᓕᕆᓂᖅ ᐊᒻᒪ ᐃᓄᓕᕆᔨᑐᖃᒃᑯᑦ ᑲᓇᑕᒥ ᐅᖃᐅᓯᐅᔪᑦ
06. Sludge Disposal
CGS Response:
A new OM plan will be prepared by the design consultant and contractor for the new 2-cell lagoon. The plan will contain a sludge management plan that includes assessment and disposal techniques, as well as a disposal location.
The upgraded lagoon will be sized to accommodate 20 years of sludge accumulation.
Effluent samples as well as visual inspection will indicate if sludge accumulates more than anticipated, and appropriate methods to remove and dispose of the sludge will be included in the new, upgraded lagoon Operation and Maintenance plan.
06. ᓴᓂᕐᓂᑦ ᐊᓂᑦᑎᓂᖅ
ᓄᓇᓕᖕᓂ ᒐᕙᒪᒃᑯᓐᓂᓗ ᐱᔨᑦᑎᕋᖅᑎᒃᑯᑦ ᑭᐅᔾᔪᑎᖓ:
ᓄᑖᖅ ᐊᐅᓚᔾᔪᑏᑦ ᐋᖅᑭᐅᒪᔾᔪᑎᓪᓗ ᐸᕐᓇᐅᑎ ᐸᕐᓇᒃᑕᐅᓂᐊᖅᑐᖅ ᐋᖅᑭᒃᓯᒪᓂᒃᓴᓕᕆᔨᒧᑦ ᐊᖏᖃᑎᒌᒃᓗᑎᒃᓗ ᐱᓕᕆᑎᑕᐅᔪᒧᑦ ᓄᑖᓄᑦ ᒪᕐᕈᐃᓕᖓᔪᓄᑦ ᑭᓈᓗᖃᕐᕕᖕᓄᑦ. ᐸᕐᓇᐅᑎ ᐃᓗᓕᖃᕐᓂᐊᖅᑐᖅ ᑭᓂᖅᑎᓯᒪᔪᒥ ᐊᐅᓚᑦᓯᓂᖅ ᐸᕐᓇᐅᑎ ᐃᓚᐅᑎᑦᑎᓗᓂ ᖃᐅᔨᓴᕈᑎᓂᒃ ᐃᒋᑦᑎᓂᕐᒧᓪᓗ ᐊᑐᕈᓯᕐᓂᒃ, ᐊᒻᒪᓗᑦᑕᐅᖅ ᐃᒋᑦᑎᕕᒃᓴᐅᑉ ᐃᓂᖓᓂ.
ᓄᑖᖑᕆᐊᖅᓯᒪᔪᖅ ᑭᓈᓗᖃᕐᕕᒃ ᐊᖏᓂᖃᖅᑎᑕᐅᓂᐊᖅᑐᖅ ᐃᓂᖃᖅᑎᓪᓗᒍ ᐊᕙᑎᑦ ᐊᕐᕌᒍᓄᑦ ᑭᓂᖅᓯᒪᔪᓂᒃ ᑲᑎᑉᐸᓪᓕᐊᑎᑦᑎᓂᕐᓂ.
ᑭᓈᓗᒃ ᑯᕕᔭᐅᓂᖓ ᑰᒻᒧᑦ ᐃᒫᓄᓪᓘᓐᓃᑦ ᖃᐅᔨᓴᒐᒃᓴᑦ ᐊᒻᒪᓗᑦᑕᐅᖅ ᑕᐅᑐᒃᓗᑎᒃ ᖃᐅᔨᓴᕈᑎᑦ ᓇᓗᓇᐃᖅᓯᓂᐊᖅᑐᑦ ᐃᒪᖅᓱᕈᖅᐸᓪᓕᐊᖕᒪᖔᑦ ᕿᓚᓈᕆᔭᐅᙱᓐᓂᖅᓴᒃᑯᑦ, ᓈᒻᒪᒃᑐᓪᓗ ᐊᑐᕈᑎᑦ ᐲᕐᓗᒋᑦ ᐃᒋᓪᓗᒋᓪᓗ ᐃᒪᖅᓱᕐᓂᑦ ᐃᓚᐅᑎᑕᐅᓂᐊᖅᑐᖅ ᓄᑖᒥ, ᓄᑖᖑᕆᐊᖅᑎᓯᒪᔪᒥᒃ ᑭᓈᓗᖃᕐᕕᖕᒥ ᐊᐅᓚᑦᑎᓂᖅ ᒪᑭᒪᑎᑦᑏᓐᓇᕐᓂᕐᓗ ᐸᕐᓇᐅᑎᖓᓂᒃ.
CIRNAC Comments

## Slide 25: ᐃᒪᕐᒥᐅᑕᓕᕆᔨᒃᑯᑦ ᑲᓇᑕᒥ ᐅᖃᐅᓯᒃᓴᖏᑦ
01. Fish Screen
CGS Response:
Information on the fish screen has been requested from the staff involved with the resupply. If the fish screen does not meet DFO requirements actions will be initiated to replace it.
01. ᐃᖃᓗᖕᓄᑦ ᓯᒥᒃ
ᓄᓇᓕᖕᓂ ᒐᕙᒪᒃᑯᓐᓂᓗ ᐱᔨᑦᑎᕋᖅᑎᒃᑯᑦ ᑭᐅᔾᔪᑎᖓ:
ᓇᓗᓇᐃᔭᐅᑎ ᐃᖃᓗᖕᓄᑦ ᓯᒥᖕᓄᑦ ᑐᒃᓯᕋᖅᑕᐅᓯᒪᔪᖅ ᐃᖅᑲᓇᐃᔭᖅᑎᓄᑦ ᐃᓚᐅᖃᑕᐅᔪᓄᑦ ᐋᖅᑭᒃᓱᐃᔪᓄᑦ. ᐃᖃᓗᖕᓄᑦ ᓯᒥᒃ ᑲᑎᒍᑎᓯᒪᙱᑦᑐᖅ ᐃᒪᕐᒥᐅᑕᓕᕆᔨᒃᑯᑦ ᑲᓇᑕᒥ ᐱᔭᕆᐊᖃᖅᑎᑕᖏᑕ ᖃᓄᐃᓕᐅᕈᑎᖏᓐᓄᑦ ᐱᒋᐊᖅᑎᑕᐅᓂᐊᖅᑐᑦ ᑭᖑᕝᕕᕐᓗᒍ.
DFO Comments

## Slide 26
ᓄᑖᖑᕆᐊᑐᑦ ᐋᖅᑭᒋᐊᖅᑕᐅᔪᖅ ᐃᒥᕐᒧ ᐱᔪᓐᓇᐅᑎ
ᐱᔭᐅᔪᒪᔪᖅ | ᓇᓗᓇᐃᖅᓯᔾᔪᑎ
ᐱᔪᓐᓇᐅᑎᖓᑕ ᐃᓱᓕᕝᕕᑦᓴᖓ: ᐅᑭᐅᓄᑦ ᖁᓕᓄᑦ | ᑖᓐᓇ ᐋᖅᑭᒋᐊᕈᑎ ᐃᓚᐅᑎᑦᑎᔪᖅ ᓄᑖᖑᕆᐊᖅᑎᑦᑎᓂᕐᓂ ᐃᒪᖃᕐᕕᖕᓂ, ᐃᒪᑦᑎᐊᕙᐅᙱᑦᑐᓂᒃ ᐃᒋᑦᑎᓂᕐᓂ, ᐊᒻᒪ ᑭᓈᓗᖕᓂᑦ ᐃᒋᑦᑎᓂᕐᓂ ᒪᑭᒪᐃᓐᓇᕈᑎᒃᓴᓂᑦ. ᐃᒥᖅᑖᕐᕕᒃ ᓂᕆᐅᒋᔭᐅᙱᑦᑐᖅ ᐅᖓᑖᓅᕐᓂᐊᕐᓗᓂ ᐃᒥᖅᑕᕐᕕᐅᑉ ᐊᖏᓂᖓᓄᑦ ᓯᕗᓂᑦᑎᓐᓂ ᐊᕐᕌᒍᑦ ᖁᓕᑦ.
ᐊᒥᓲᓛᖑᔪᓐᓇᕐᑐᑦ ᐊᕐᕌᒍᓕᒫᖅᓯᐅᑎᑦ ᐃᒥᕐᒧᑦ: 235,393 m3 | ᐃᒪᓕᕆᕝᕕᖕᒥ ᐊᖏᓂᖓ 235,393 m3 ᐊᑑᑎᖃᕐᓂᐊᖅᑐᖅ ᐱᖃᖅᑎᓪᓗᒍ Hᐋᒻᒪᓚᒃᑯᑦ ᐊᒃᓱᓪᓘᓐᓃᑦ 2034 ᑐᙵᕕᖓᓂ ᐋᖅᑭᒃᓯᒪᓂᒃᓴᖓᑕ ᓈᓴᐅᓯᕆᔾᔪᑎᖏᓐᓂ.
Request | Justification
Licence Term: 10 years | This amendment includes upgrades to the water supply, wastewater disposal, and solid waste disposal infrastructure. The water consumption is not expected to exceed the reservoir capacity in the next 10-years.
Maximum Annual Water Withdrawal: 235,393 m3 | The reservoir capacity 235,393 m3 will be sufficient to supply the municipality until at least 2034 based on design calculations.
Renewals and Amendments for the Water License

## Slide 27
ᓄᑖᖑᕆᐊᑐᑦ ᐋᖅᑭᒋᐊᖅᑕᐅᔪᖅ ᐃᒥᕐᒧ ᐱᔪᓐᓇᐅᑎ
ᐱᔭᐅᔪᒪᔪᖅ | ᓇᓗᓇᐃᖅᓯᔾᔪᑎ
ᐊᓯᔾᔨᕈᑎᑦ ᖃᐅᔨᓴᕈᑎᒃᓴᓄᑦ ᐱᓕᕆᐊᒃᓴᒥ | ᐃᒪᖃᕐᕕᖓ ᐊᑎᖃᖅᑎᑕᖅ ᐊᒪᕈᖅ ᑰᕈᖅ
 | ᐱᓗᐊᙱᑦᑐᖅ ᐅᓗᕆᐊᓇᖅᑐᖅ ᐲᖅᑕᐅᓪᓗᓂ ᐊᓯᖏᓐᓂ ᓄᓇᕗᒻᒥ Hᐋᒻᒪᓚᒃᑯᑦ ᐃᒪᕐᒧᑦ ᐱᔪᓐᓇᐅᑎᓂ ᐱᓪᓗᒍ ᓈᒻᒪᙱᓐᓂᕋᖅᑕᐅᓂᖏᓐᓄᑦ ᐅᑭᐅᖅᑕᖅᑐᒥ ᓄᓇᓕᖏᓐᓄᑦ ᐊᑐᐊᒐᓕᐅᖅᑎᓄᑦ.
 | ARV-3 ᖃᐅᔨᓴᕐᓗᑎᒃ ᑲᑉᐳᔾᔭᖅᑐᖏᓐᓂᒃ ᑭᓈᓗᖃᕐᕕᒃ ᖃᐅᔨᓇᓱᐃᓐᓇᕐᓗᑎᒃ ᐋᖅᑭᒋᐊᖅᑕᐅᑦᑎᐊᖅᓯᒪᖕᒪᖔᑕ.
 | ᐲᕐᓗᒍ ARV-7 ᐆᒻᒪᖅᑯᑎᒃᓴᓕᐅᖅᓯᒪᔪᓂᒃ ᖃᐅᔨᓴᕐᓂᖅ ᐊᒪᕈᖅ ᑰᕈᖅ ᐃᑲᔪᕈᓐᓇᕐᓂᖓᓂᒃ ᐱᑲᓐᓂᕈᑎᓂᒃ 0.22% ᑯᕕᔪᒥᒃ.
 | ᐲᕐᓗᒍ ARV-8 ᓇᓃᓐᓂᖓ ᖃᐅᔨᓴᖅᑕᐅᖃᑦᑕᕐᓂᖓᓄᑦ ᐊᕐᕌᒍᑕᒫᑦ ᑭᓈᓗᖃᕐᕕᐅᑉ ᐊᔪᙱᓐᓂᖓᓂ ᐋᖅᑭᒃᓯᒪᑎᓪᓗᒍ ᐊᑕᐅᓯᖅ ᒦᑕ ᐊᕙᓗᖓᑕ ᑕᑭᓂᖓᒍᑦ.
 | ᐲᕐᓗᒍ ARV-10 ᐊᒻᒪ ARV 11 ᓲᖃᐃᒻᒪ ᐱᑕᖃᙱᒻᒪᑕ.
Request | Justification
Changes to the Sampling Program | The water source is named Wolf Creek
 | Acute toxicity was removed from other Nunavut municipal water licences due to being deemed inappropriate for northern jurisdictions by the regulators.
 | ARV-3 to test at the outlet of the lagoon to monitor treatment efficacy.
 | Remove ARV-7 as the hydrology study demonstrated Wolf Creek can support the resupply which is 0.22% of flow.
 | Remove ARV-8 since level is monitored annually by the lagoon’s ability to maintain 1 m freeboard
 | Remove ARV-10 and ARV 11 because they do not exist.
Renewals and Amendments for the Water License

## Slide 28
ᓄᑖᖑᕆᐊᑐᑦ ᐋᖅᑭᒋᐊᖅᑕᐅᔪᖅ ᐃᒥᕐᒧ ᐱᔪᓐᓇᐅᑎ
ᐱᔭᐅᔪᒪᔪᖅ | ᓇᓗᓇᐃᖅᓯᔾᔪᑎ
ᑭᓈᓗᒃ ᑯᕕᔭᐅᓂᖓ ᑰᒻᒧᑦ ᐃᒫᓄᓪᓘᓐᓃᑦ ᖃᐅᔨᓴᖅᑕᐅᔪᒧᑦ ᖃᐅᔨᓴᖅᑕᐅᖃᓯᐅᑎᒋᐊᓖᑦ ᐃᓱᐊᓂ ᐃᒪᖅᓱᙳᖅᑎᓗᐊᔾᔭᐃᒃᑯᑎ | ᐊᓯᔾᔨᕐᓗᒍ ᐃᓚᐅᕈᑎ ᐆᒪᔪᓄᑦ ᐊᓂᖅᑎᕆᔭᐅᖃᑦᑕᖅᑐᓄᑦ ᐱᔪᒪᔭᐅᓂᖓ ᐃᓱᖃᕐᕕᖓ 100 mg/L ᐊᒻᒪ ᑲᑎᖦᖢᒋᑦ ᓄᖅᑲᖓᑎᑕᐅᔪᖅ ᑭᓈᓗᖕᓄᑦ ᐃᓱᖃᕐᕕᖓ 120 mg/L; ᓇᓃᓐᓂᖏᑦ ᐱᑎᑕᐅᔪᑦ ᐊᕐᕌᒍᒐᓴᖕᓄᑦ ᓄᓇᕗᒻᒦᑦᑐᓂ ᑭᓈᓗᖃᕐᕕᒃ ᐃᒪᖅᓲᓗᐊᖅᑎᑦᑎᑕᐃᓕᓂᕐᒧᑦ ᖃᐅᔨᓴᕈᑎᒥᑦ.
ᐲᕐᓗᒋᑦ ᖃᐅᔨᒪᓇᕈᑎᑦ “ᐅᓗᕆᐊᓇᖅᑐᓄᑦ ᐊᒃᑐᖅᑕᐅᓯᒪᔪᑦ ᓱᕈᖅᓯᒪᔪᓂ ᐃᔾᔪᒃᑯᕕᒃ ᐊᒻᒪ ᐋᖅᑭᒋᐊᕐᕕᖕᓂ” ᐊᒻᒪᓗ “ᓄᑖᖅ ᑕᖏᓕᖕᓄᑦ ᐊᒃᑕᕐᕕᒃ” | ᑖᒃᑯᐊ ᐱᓕᕆᕖᑦ ᐱᑕᖃᙱᑦᑐᑦ.
Renewals and Amendments for the Water License
Request | Justification
Effluent Parameters at the end of the wetland-treatment-area | Change CBOD limit to 100 mg/L and Total Suspended Solid limit to 120 mg/L; levels are based off of the multi year Nunavut based lagoon-wetland treatment research.
Remove references to “Hydrocarbon Impacted Soil Storage and Treatment Facility” and “New Solid Waste Disposal Facility” | These facilities do not exist.

## Slide 29
ᓄᑖᖑᕆᐊᑐᑦ ᐋᖅᑭᒋᐊᖅᑕᐅᔪᖅ ᐃᒥᕐᒧ ᐱᔪᓐᓇᐅᑎ
ᐱᔭᐅᔪᒪᔪᖅ | ᓇᓗᓇᐃᖅᓯᔾᔪᑎ
ᐲᕐᓗᒋᑦ ᐱᔭᕆᐊᓕᑦ ᐊᕐᕌᒍᑕᒫᑦ ᓄᓇᓕᕆᔾᔪᑎᑦ ᖃᐅᔨᓴᖅᑐᓕᕆᓂᙶᖅᑐᓂᒃ ᐊᑐᖅᑎᑦᑎᔪᓐᓇᖅᑐᖅ ᖃᐅᔨᓴᕈᑎᓂ | ᐃᖅᑲᓇᐃᔭᖅᑎᑦᑎᓂᖅ ᓄᓇᓕᕆᔾᔪᑎᑦ ᖃᐅᔨᓴᖅᑐᓕᕆᓂᙶᖅᑐᓂᒃ ᐊᑐᖅᑎᑦᑎᔪᓐᓇᖅᑐᖅ ᐱᓕᕆᐊᖃᕐᓗᓂ ᐊᕐᕌᒍᑕᒫᖅᓯᐅᑦ ᖃᐅᔨᓴᕐᓂᕐᒥᒃ ᐊᑐᖅᑕᐅᔭᕆᐊᖃᓪᓚᕆᙱᑦᑐᖅ ᐃᑲᔪᖅᓱᖅᑕᐅᙱᖦᖢᓂᓗ ᑖᒻ ᐊᑦᑕᕐᓇᖅᑕᐃᓕᒪᓂᕐᒧᑦ ᒪᓕᒋᐊᓕᖕᓂ (CDA, 2013).
ᐲᕐᓗᒋᑦ ᐅᖃᐅᓯᖃᑦᑎᐊᖅᓯᒪᔪᑦ ᐱᖁᔭᐅᓯᒪᔪᑦ ᖃᓄᖅ ᐃᓂᑐᖃᖓᓄᑦ ᐅᑎᖅᑎᑦᑎᓂᖅ ᐊᑐᖅᑕᐅᔪᓐᓃᖅᑐᓂᒃ ᐱᓕᕆᕕᖕᓂ | ᐱᔪᓐᓇᐅᑎᓕᕆᔨᒻᒪᕆᑦ ᐱᒋᐊᖅᑎᑦᑎᓇᔭᖅᑐᑦ ᓈᒻᒪᒃᑐᓂᒃ ᐋᖅᑭᒋᐊᖅᑕᐅᓂᖏᓐᓂ ᖃᓄᐃᓕᐅᕈᑎᓂᑦ
Request | Justification
Remove requirement for annual geotechnical engineer inspection | Hiring a geotechnical engineer to conduct an annual inspection is not practical and is not supported by the Dam Safety Guidelines (CDA, 2013).
Remove prescriptive recommendations on how to carry out reclamation of abandoned facilities | Licenced professionals will dictate appropriate remediation activities
Renewals and Amendments for the Water License

## Slide 30
ᓄᑖᖑᕆᐊᑐᑦ ᐋᖅᑭᒋᐊᖅᑕᐅᔪᖅ ᐃᒥᕐᒧ ᐱᔪᓐᓇᐅᑎ
ᐱᔭᐅᔪᒪᔪᖅ | ᓇᓗᓇᐃᖅᓯᔾᔪᑎ
ᐲᕐᓗᒍ ARV-7 | ᐆᒻᒪᖅᑯᑎᒃᓴᓕᐅᖅᓯᒪᔪᓂᒃ ᖃᐅᔨᓴᕐᓂᖅ ᐱᔭᕇᖅᑕᐅᓪᓗᓂ ᐊᒪᕈᖅ ᑰᕈᕐᒥ ᓇᓗᓇᐃᖅᓯᓪᓗᓂ ᐊᕐᕌᒍᑕᒫᖅᓯᐅᑦ ᐱᖃᒃᑲᓐᓂᕐᓂᖅ ᐊᑐᕐᓂᕐᓂ 0.22% ᑰᕈᔪᒃᓗᓂ. ᐃᒪᕐᒥᐅᑕᓕᕆᔨᒃᑯᑦ ᑲᓇᑕᒥ ᐱᔪᓐᓇᖅᑎᑦᑎᔪᑦ 10% ᐲᖅᓯᓂᕐᒥ. ᐱᔪᓐᓇᐅᑎᑖᖅᓯᒪᓂᕐᒧᑦ ᑐᒃᓯᕋᖅᑕᖅ ᑖᓐᓇ ᖃᓄᐃᓕᖓᓂᖅ ᐲᖅᑕᐅᓗᓂ ᐱᔪᓐᓇᐅᑎᑖᖅᓯᒪᑎᑦᑎᔨ ᓇᓗᓇᐃᔭᐃᓯᒪᓂᖓᓄᑦ ᐃᒪᖅ ᐃᑲᔪᕈᓐᓇᖅᑐᖅ ᐊᕐᕌᒍᑕᒫᖅᓯᐅᑦ ᐃᒥᖅᑕᕐᕕᖕᒥ ᐱᖃᖅᑎᑦᑎᒃᑲᓐᓂᕐᓂᕐᒥᒃ.
ᐲᕐᓗᒍ ARV-8 | ᖃᓕᕇᖕᓂᖓ ᖃᐅᔨᓴᖅᑕᐅᙱᓐᓇᓲᖅ, ᐃᖅᑲᓇᐃᔭᖅᑎᓄᑦ ᐊᒻᒪ ᑯᐄᓐ ᑭᒡᒐᖅᑐᖅᑎᖓ−ᓄᓇᖃᖅᑳᖅᓯᒪᔪᓕᕆᓂᖅ ᐊᒻᒪ ᐃᓄᓕᕆᔨᑐᖃᒃᑯᑦ ᑲᓇᑕᒥ ᖃᐅᔨᓴᖅᑎᒧᑦ ᑭᓈᓗᖃᕐᕕᐅᑉ ᐱᔪᓐᓇᖅᑕᖓᒍᑦ ᐋᖅᑭᒃᓯᒪᑎᓪᓗᒍ 1 ᒦᑕ ᐊᕙᓗᖓᑕ ᑕᑭᓂᖓᒍᑦ.
Renewals and Amendments for the Water License
Request | Justification
Remove ARV-7 | The hydrology study was done on Wolf Creek indicated the annual reservoir resupply uses 0.22% of the flow. DFO allows up to 10% withdrawal. The licensee requests that this condition be removed since the licensee has demonstrated the water source can support the annual reservoir resupply.
Remove ARV-8 | The Level is monitored, by staff and the CIRNAC inspector through the lagoon’s ability to maintain 1 m freeboard.

## Slide 31
ᐱᔭᐅᔪᒪᔪᖅ | ᓇᓗᓇᐃᖅᓯᔾᔪᑎ
ᐲᕐᓗᒍ ᐱᔭᕆᐊᖃᖅᑎᑕᖅ ᐱᓇᓱᐊᕈᓯᑕᒫᒃᑯᑦ ᖃᐅᔨᓴᕐᓂᕐᒧᑦ ᖃᐅᔨᓴᐃᓐᓇᕐᓂᕐᒧᑦ ᐱᓕᕆᐊᒃᓴᖅ ᐱᓕᕆᕕᖕᓂ | ᑖᓐᓇ ᐱᔭᕆᐊᓕᒃ ᒪᓕᑦᑎᐊᙱᑦᑐᖅ ᐊᓯᖏᓐᓂ ᓄᓇᕗᒻᒥ ᐃᒪᕐᒧᑦ ᑲᑎᒪᔩᑦ ᑲᔪᓯᑎᑕᖏᓐᓂ ᐃᒪᕐᒧᑦ ᐱᔪᓐᓇᐅᑎᓂ. ᖃᐅᔨᓴᐃᓐᓇᕐᓂᕐᒧᑦ ᐱᓕᕆᕖᑦ ᖃᐅᔨᓴᐃᓐᓇᕐᕕᐅᒐᔪᒃᑐᑦ, ᐅᓄᖅᓱᐃᖅᖢᑎᒃ ᐱᓇᓱᐊᕈᓯᕐᒥ, ᐃᑲᕐᕋᐅᒐᔪᒃᑐᒃᑯᑦ Hᐋᒻᒪᓚᒃᑯᑦ ᐊᐅᓚᓂᖏᑎᒍᑦ ᖃᐅᔨᓴᕈᑎᒃᓴᓪᓗ ᐱᒋᐊᕐᖢᑎᒃ ᑰᓕᕌᖓᑦ. ᐸᕐᓇᐃᓂᖅ ᐱᓇᓱᐊᕈᓯᑕᒫᑦ ᐅᓂᒃᑳᒥᒃ ᑕᖃᓇᓗᐊᕐᒪᑦ ᐃᖅᑲᓇᐃᔭᖅᑎᓄᑦ.
ᐊᓯᔾᔨᕐᓗᒍ ᖃᐅᔨᓴᕈᑎᒃᓴᓂ “ᒪᐃ−ᐊᐅᒍᓯ” ᐅᕗᖓ “ᑕᖅᑭᑕᒫᑦ ᒪᙳᒃᓯᒪᓐᓇᖅᑎᓪᓗᒍ. | ᒪᙳᖃᑦᑕᙱᑦᑐᖅ ᑎᑭᓐᓇᓱᖕᓂᖓᓂ ᔫᓂ ᔪᒪᐃᓘᓐᓃᑦ ᖁᐊᕈᑎᓪᓗᑎᒃᓗ ᓄᖑᓕᖅᑎᓪᓗᒍ ᓯᑎᐱᕆ ᐅᑐᐱᕆᓘᓐᓃᑦ ᐊᕐᕌᒍ ᒪᓕᒃᖢᒍ.
ᓄᑖᖑᕆᐊᑐᑦ ᐋᖅᑭᒋᐊᖅᑕᐅᔪᖅ ᐃᒥᕐᒧ ᐱᔪᓐᓇᐅᑎ
Renewals and Amendments for the Water License
Request | Justification
Remove requirement for weekly inspection of Monitoring Program Stations | This requirement is inconsistent with other NWB issued water licences. The monitoring stations are regularly monitored, multiple times a week, during regular municipal operations and sampling begins when flow is present. Preparing a weekly report is too high of a burden on staff.
Change sampling “May-August” to “Monthly during thawed conditions” | Thaw typically does not occur until June or July and freeze-up may be as late as September or October depending on the year.

## Slide 32
ᓄᑖᖑᕆᐊᑐᑦ ᐋᖅᑭᒋᐊᖅᑕᐅᔪᖅ ᐃᒥᕐᒧ ᐱᔪᓐᓇᐅᑎ
ᐱᔭᐅᔪᒪᔪᖅ | ᓇᓗᓇᐃᖅᓯᔾᔪᑎ
ᐲᕐᓗᒍ ᐱᓗᐊᙱᑦᑐᓂ ᑐᖁᓐᓇᖅᑑᔪᓐᓇᖅᑐᓂ ᖃᐅᔨᓴᕐᓂᖅ | ᐊᕙᑎᒧᑦ ᓯᓚᐅᑉ ᐊᓯᔾᔨᖅᐸᓪᓕᐊᓂᖓᓄᑦ ᑲᓇᑕᒥ ᐃᓕᓴᖅᓯᓯᒪᔪᑦ ᑖᓐᓇ ᖃᐅᔨᓴᕈᑎ ᐱᔭᕆᐊᖃᓪᓚᕆᙱᑦᑐᖅ ᐅᑭᐅᖅᑕᖅᑐᒥ ᓄᓇᓕᕋᓛᖑᓂᖅᓴᐅᔪᓄᑦ, ᐲᖅᑕᐅᓯᒪᓪᓗᓂᓗ ᐊᓯᖏᓐᓂ ᐱᔪᓐᓇᐅᑎᓂ.
ᐲᕐᓗᒍ ᐱᔭᕆᐊᖃᖅᑕᐅᔪᖅ ᑐᓂᓯᓗᓂ ᑎᑎᖅᑲᑦ ᐊᔾᔨᖏᓐᓂ | ᖃᕆᑕᐅᔭᒃᑯᑦ ᑐᓂᓯᓂᖅ ᒪᓕᒋᐊᖃᖅᑕᐅᓪᓗᓂ ᐊᑐᕋᓲᑎᐅᔪᖅ.
Renewals and Amendments for the Water License
Request | Justification
Remove acute lethality testing | ECCC has recognized that this test is not practical for remote northern communities and it has been removed from other licences.
Remove the requirement to submit paper copies | Electronic submission is standard practice.

## Slide 33
ᐃᓱᐊ
The End