## page 1
No. | Category | Comment | Subcomment | Assigned to | Response | Associated Attachment
1 | Source of Gravel and Clay Materials | The source of gravel and clay to be used in the new landfill has not yet been shared with the public, as indicated in Question 8 of the Consultation Record. An understanding of the source of building materials is helpful for reviewers to assess full impact of the construction of infrastructure, and for understanding topographical specifications at the quarry site which relate to surface water quality and flow management. | (IR-01) CIRNAC requests that the source of the gravel and clay be communicated with CIRNAC as soon as a location is chosen by the City of Iqaluit. | Colliers/City | It is understood that the City/Colliers/EXP have granular sources identified for the landfill and access road and will respond to this comment. EXP Response: see attached email correspondence and attached License No. 8BW-IGD1921 issued to City of Iqaluit by the Nunavut Water Board for an access road to new gravel source. | Attachment - PDF Document: 190508 8BW-IGD1921 Licence-ODDE & Email Correspondence: Dillon Consulting Limited Mail - RE_ Iqaluit Liner Lowered by 2 and 4m
2 | Erosion and Sediment Control Plan | The Erosion and Sediment Control Plan describes control measures to be implemented by the City of Iqaluit to reduce the risk of sediment transport off site and into nearby water bodies. The Erosion and Sediment Control Plan covers all phases of the project for the Waste Transfer Station and for the Landfill, but does not describe measures to be undertaken regarding the access road. | (IR-02) CIRNAC recommends that the City of Iqaluit include a section in the Erosion and Sediment Control Plan to indicate the risks and mitigation measures for sedimentation and erosion along the access road. | EXP | EXP Response: I assume this question is referring to the attached 2014 report updated March 2019. We feel that section 5 of the report provides that information. | Attachment - PDF Document: 2019-03-26 Spill Response and Erosion and Sediment Conrol Plan_fnl-revised contact info
3 | Inclusion of Landfill in City Management Plans Previously Submitted | The City of Iqaluit is currently working with Nunami Stantec on a Master Drainage Plan for the City of Iqaluit. The new landfill will require water services from the City and surface water management for precipitation and overland flow events. CIRNAC recommends that the landfill and associated infrastructure be included in the Master Drainage Plan. Further, CIRNAC recommends that landfill operations, including contact water, sediment water, fuels, leachate, and hazardous wastes, be included and/or updated in the Spill Contingency Plan. | (IR-03) CIRNAC requests that the City of Iqaluit indicate if, when, and how the Master Drainage Plan and the Spill Contingency Plan will be updated to include measures pertaining to the new landfill, the waste transfer station, and the landfill access road. | EXP / Dillon | Spill Contingency Plan will be updated in the 100% submission to include measures pertaining to the new landfill, the waste transfer station, and the landfill access road.
4 | Geotechnical Study for the Access Road | The Statement of Construction Report indicated completed studies which have not yet been made available for intervener review. These studies were the Geothermal Modelling and Geotechnical Recommendations Transfer Station and Landfill in Iqaluit, Nunavut May 2019, the City of Iqaluit Geotechnical Investigation Proposed Waste Transfer Station Lots 3586 228/17/18/20 and 3480 220 1, Iqaluit, Nunavut, October, 2018, and a Quality Control Program. The Statement of Construction Report also indicated planned programs, such as regular safety audits. One important study which was not indicated was a geotechnical study for the proposed access road. CIRNAC would find it beneficial to know whether a geotechnical study for the access road has been completed or if one is planned. | (IR-04) CIRNAC requests that the City of Iqaluit clarify whether a geotechnical study has been completed, or is planned for the access road, and that all the indicated studies and programs be made available during the technical review phase. | EXP | EXP Response: exp did not complete a geotechnical study of the access road. Colliers: We have received a Geo Report from EXP in an email dated May 7, 2020. See Report Attached. We have also received a preliminary geo report for the landfill Site | Attachment - PDF Document: 2015.01.29_GeoInvRpt_NWAggregateDeposit_IqaluitNU & 2020.01.28_PreliminaryGeoInvRpt_LandfillSite_Iqaluit_NU
5 | National Building Code of Canada (NBCC 2015) | The National Building Code of Canada (National Research Council Canada, 2015) outlines technical provisions for the design and construction of new buildings, and for the alteration, change of use, and demolition of existing buildings. Different editions of this code exist for different jurisdictions. | (IR-05) CIRNAC recommends that the City of Iqaluit clarify and confirm whether all the structural reinforcement details such as concrete wall details, concrete mat foundation, and so on, meet the minimum requirements of the National Building Code of Canada (National Research Council Canada, 2015), or the minimum requirements of the territorial edition of the code which apply to buildings in Nunavut. | Dillon | The design of the structure is in conformance with the NBC 2015. The design of concrete structure is in conformance with the CSA A23.3. Nunavut adopts the NBC 2015. Thermosyphon design is in accordance with CSA S500.
6 | Method Statement of Construction Report | The Method Statement of Construction Report describes the construction methodology to be used for the proposed new Iqaluit Landfill and Waste Transfer Station. CIRNAC recommends that the report be updated with additional information regarding grading, drainage, and erosion of the access road to provide full details of construction so that intervener can conduct adequate technical reviews of the methods and impacts. | (IR-06) CIRNAC requests that the City of Iqaluit consider adding the following sections to the Method Statement of Construction Report: |  | EXP Response: my understanding from our Ottawa office is that exp’s preliminary construction report and tender specs for the access road was provided by Colliers to Dillion to include in their work. Colliers: Dillion has confirmed receiving these documents
|  |  | i. An erosion and sediment control section under the Landfill Access Road construction section (Section 6.0); and | EXP | Colliers: Noted, passed onto EXP and Dillion to be addressed in 100% design submission
|  |  | ii. Additional information regarding the grading and drainage components of the new access road, such as ditching and culvert installation, under the Scope of Work (Section 6.2.3). | EXP | Colliers: Noted, passed onto EXP and Dillion to be addressed in 100% design submission
7 | Closure and Decommissioning Plan | The Closure and Decommissioning Plan, associated with Block 9 of the Application Form - Description of Undertaking, provide plans for the closure of the Landfill infrastructure. Upon review CIRNAC developed a number of questions. These are indicated in the information request. | (IR-07) CIRNAC recommends that the City of Iqaluit provide the following information in the Closure and Decommissioning Plan:
|  |  | i. Information on if and how the leachate retention ponds will be de-commissioned at the end of the 75 year cycle; | Dillon | There is a strong possibility that even after the landfill's 75 year life, leachate will continue to be generated for several years or decades post-closure. Once the holding ponds are no longer required, the liner material will be removed and disposed of at an approved location. The ponds will either then need to be filled in with clean fill material, or the berms deconstructed and disposed of, depending on land use requirements.
|  |  | ii. Information on if and how the leachate ponds will be covered by protected shield; | Dillon | There is no protective covering proposed for the leachate holding ponds. Such a cover would be difficult to maintain and likely require frequent replacement/repair. Similar to the West 40 site, the lagoon will be fenced in.
|  |  | iii. Information on if and how wildlife, including birds will be prevented from entering the leachate retention ponds during normal operation of the landfill; | Dillon | It is Dillon's understanding that during the previous landfill siting project, consideration was given to Transport Canada's siting requirements for solidwaste and liquid waste disposal sites in regards to airports. For operational purposes, some wildlife will be kept out via fence, while other vectors (such as birds) may require deterrence through audio means (i.e. noise bangers, drones).
|  |  | iv. Information on if and how wildlife, including birds, be prevented from entering the leachate retention ponds at closure and decommissioning; and, | Dillon | Post-closure, the lagoons will be pumped out, cleaned (with leachate-bearing materials disposed of in accordance with regulatory requirements) and filled in.
|  |  | v. Given a certain level of anticipated settlement in the final grading of the site, whether a survey of the site will be completed, and if so at what frequency. | Dillon | A survey of the LF base should be conducted at the time of contruction followed by subsequent annual surveys of the landfill cap to ensure water is being directed away from the deposit?
8 | Design Drawing Details | The design drawing packages WTS – 90 Percent Drawings and Landfill – 90 Percent Drawings, are associated with Block 9 of the Application Form - Description of Undertaking. These packages provide plans for the construction of the Waste Transfer Station and Landfill infrastructure. The Engineering Drawings provided are preliminary and not intended for construction. Upon CIRNAC review, a number of items are noted which are recommended to be added to the drawings for construction purposes. These are indicated in the information requests. | (IR-08) CIRNAC recommends that the City of Iqaluit indicate the following items on the Waste Transfer Station Drawings:
|  |  | i. The party responsible for the development of the required specifications on the Design Drawings (ex. materials and performance ratings); | Dillon | Where appropriate, drawings will be stamped by the party responsible
|  |  | ii. The maintenance routine in order to address any defects of the planned shallow trench around the perimeter of the baling unit; | Dillon | Will be addressed in the 100% report submission
|  |  | iii. The material and method of construction of the indicated trench; | Dillon | Will be addressed in the 100% report submission
|  |  | iv. Details of the Weigh Scale House including location, heating, and ventilation systems; | Dillon | Details to be provided in 100% drawing and spec submission
|  |  | v. Details about the emergency generator, including location of storage tank, day tank and piping; | Dillon | Only one tank provided and it will under the generator in the enclosure. Generator Specification to be added to 100% submission
|  |  | vi. Emergency generator on equipment schedule; | Dillon | No equipment schedule for the generator. Generator specification to be added
|  |  | vii. Location of fuel storage tanks for fuelling of vehicles; | Dillon | No vehicle fueling on the project
|  |  | viii. Details of the glycol loop; and | Dillon | Assume CIRNAC is referencing the thermosyphon piping as there is no glycol loops, additional thermosyphon design will be provided in 100% drawing set. Thermosyphone design is as per CSA S500. Supplier will provide sealed construction drawings.
|  |  | ix. The location of the glycol pump on the pump schedule. | Dillon | Thermosyphone does not require pump. It requires radiators which are at the manifold pads as per drawings.
(IR-09) CIRNAC also recommends that the City of Iqaluit indicate the following items on the Landfill Drawings:
|  |  | i. Details of the leachate pumping station, which is indicated in the Method Statement of Construction Report. | Dillon | Will be addressed in the 100% report submission
9 | Operation and Maintenance Manual | The Operations and Maintenance Manual (O&M Manual) describes the details and procedures for staff to follow to maintain the facility in safe and efficient state so that operations run smoothly and equipment functions to the best of its ability. CIRNAC has reviewed the O&M Manual and did not find a schedule for reviews of certain project components. To maintain peak performance, CIRNAC recommends including periodic reviews of the condition of the access road to ensure that there are no major depressions and that the grading allows for a proper drainage management. Further, given that permanent erosion and sediment control measures are to be put in place, CIRNAC recommends including a periodic review of these components in the O&M manual. | (IR-10) CIRNAC recommends that a schedule or trigger for periodic reviews be written into the O&M Manual for the condition of the access road and for the erosion and sediment control measures put in place. | Dillon | Will be addressed in the 100% report submission
Nunavut Water Board
1 | Leachate treatment options evaluation memo | As described in the Method Statement of Construction report, leachate will be collected via the landfill’s liner system and then pumped to the leachate collection facility. Section 5.2.12 of this report indicates that on August 30, 2019, Dillon Consulting submitted a leachate treatment options evaluation memo to the City of Iqaluit. This memo apparently presented several options for leachate treatment at the new landfill. This memo does not appear to be included in the water licence amendment application. Submission of this memo is important to support an understanding of leachate treatment options. | ECCC requests that the leachate treatment options evaluation memo that was submitted by Dillon Consulting to the City of Iqaluit on August 30, 2019 be provided for review. | Dillon | Please see attached memo. The results of the investigation recommended three different approaches, essentially based on the reuse (or partial reuse) of existing equipment. After discussion with the City and their representatives, due to capital cost requirements and the uncertainty in leachate quality, Dillon was directed to design the holding ponds to store leachate for approximately two years until the landfill is established. | Attachement PDF Document: Iqaluit Leachate Memo, 30Aug2019
2 | Monitoring and Inspection | Both of the Environmental Protection Plans (i.e., EPP - Construction Phase; and EPP - Operations, Closure and Post-Closure Phases) lack sufficient information on monitoring and inspection activities. Section 5.0 (Monitoring and Inspection) of both plans is a single short paragraph which concludes “There may be a need to revise specific monitoring and inspection activities outlined below…”. However, neither document outlines monitoring and inspection activities. | ECCC recommends that the proponent update Section 5.0 (Monitoring and Inspection) of both Environmental Protection Plans (i.e., EPP - Construction Phase; and EPP - Operations, Closure and Post-Closure Phases) to specify the monitoring and inspection activities that will be conducted. | Dillon | Reports will be updated for the final 100% submission