## Raw water (A)
Table 1: Raw Water Quality (WTP)
Nunavut Water Board Licence 3AM-IQA0611 |  |  |  |  | Lab I.D. | 974525 | 986505 | 993858 | B13-15205-1 | B13-17498-1 | B13-22716-1/2 | B13-26553-1 | B14-15360-1 | B14-19763-1 | B14-23242-1 | B14-25348-1
City of Iqaluit |  |  |  |  | Sample Matrix | Water | Water | Water | Water | Water | Water | Water | Water | Water | Water | Water
Sample Type
[5 empty] | Sampling Date | 2012-07-25 | 2012-09-19 | 2012-10-25 | 2013-06-18 | 08-Jul-13 | 2013-08-27 | 2013-10-07 | 2014-06-24 | 05-Aug-14 | 29-Aug-14 | 29-Sep-14
[5 empty] | Sample I.D. | Raw | Test A (WTP Raw) | City of Iqaluit |  | WTP Test A | WTP Test A | WTP Test A | Test A | Test A | Test A - WTP | Test A - WTP
Group | Analyte | MRL | Units | CCME | Guidelines for Canadian Drinking Water Quality
Water Quality Objectives
General Chemistry and Nutrients | Hardness as CaC03 | 1 | mg/L | NV | NV | 12 | 19 | 22 | 27 | 16 | 15 | 17 | 26 | 15 | 15 | 16
| Alkalinity as CaC03 | 5 | mg/L | NV | NV | 15 | 21 | 22 | 24 | 13 | 14 | 14 | 21 | 11 | 12 | 14
| Bicarbonate (HC03 as CaC03) | 1 | mg/L | NV | NV | 15 | 21 | 22 | 24 | 13 | 14 | 14 | 21 | 11 | 12 | 14
| Carbonate as CaC03 | 5 | mg/L | NV | NV | <5 | <5 | <5 | <5 | <5 | <5 | <5 | <5 | < 5 | < 5 | < 5
| Hydroxide |  | mg/L | NV | NV | NA | NA | NA | <5 | <5 | <5 | <5 | <5 | < 5 | < 5 | < 5
| pH | 1 |  | 6.5 - 9 | 6.5 - 8.5 | 6.76 | 6.68 | 6.51 | 7.14 | 7.13 | 7.18 | 7.19 | 7.12 | 7.09 | 7.1 | 7.26
| Conductvity | 1 | umho/cm | NV | NV | 38 | 45 | 49 | 63 | 37 | 37 | 38 | 61 | 33 | 32 | 36
| Total Dissolved Solids (TDS) | 1 | mg/L | NV | 500 (AO) | 25 | 29 | 32 | 31.7 | 19.3 | 18.4 | 19 | 29.7 | 16.5 | 17.1 | 18
| Total Suspended Solids (TSS) | 2 | mg/L | NV | NV | <2 | 70 | <2 | <3 | <3 | 3 | 3 | <3 | < 3 | 10 | < 3
| Chloride | 1 | mg/L | 120 (long term), 640 (short term) | 250 (AO) | 1 | 1 | 1 | 1.6 | 1.5 | 1.2 | 1.1 | 1.6 | 1.1 | 1 | 1
| Sulphate (S04) | 3 | mg/L | NV | 500 (AO) | 3 | 4 | 4 | 4 | 3 | 2 | 3 | 4 | 2 | 2 | 2
| o-Phosphate (P) | 0.01 | mg/L | NV | NV | NA | NA | NA | <0.01 | <0.1 | <0.01 | <0.01 | <0.01 | < 0.01 | < 0.01 | < 0.01
| BOD | 3 | mg/L | NV | NV | NA | NA | NA | <3 | <3 | NA | NA | NA | < 3 | NA | NA
| Total Organic Carbon (TOC) | 0.5 | mg/L | NV | NV | 2.4 | 2.6 | 2.5 | 2.2 | 2.5 | 3.1 | 3.1 | 1.5 | 1.8 | 2.5 | 2.3
| Total Inorganic Carbon | 2 | mg/L | NV | NV | 3.7 | 3.4 | 3.9 | 5.1 | <0.5 | 3.1 | 3.3 | 5.9 | 3.1 | 3.1 | 3.8
| Turbidity | 2 | mg/L | NV | 0.1 (Treated) | NA | NA | NA | 1 | 0.6 | 1.2 | 1 | 0.4 | 0.9 | 0.7 | 0.7
Mercury | Mercury (Hg) | 0.0001 | mg/L | 2.6e-05 | NV | <0.0001 | <0.0001 | <0.0001 | NA | NA | NA | NA | NA | NA | NA | NA
Metals | Aluminum (Al) | 0.01 | mg/L | 0.1 | 0.1 | <0.01 | <0.01 | <0.01 | <0.01 | 0.03 | 0.04 | 0.02 | 0.01 | 0.02 | 0.02 | 0.01
| Antimony (Sb) | 0.0005 | mg/L | NV | 0.006 | <0.0005 | <0.0005 | <0.0005 | 0.003 | < 0.0005 | <0.0001 | 0.0001 | <0.0005 | < 0.0005 | < 0.0005 | 0.0006
| Arsenic (As) | 0.01 | mg/L | 0.005 | 0.01 | <0.001 | <0.001 | <0.001 | 0.0001 | < 0.0005 | <0.0001 | <0.0001 | <0.0005 | < 0.0005 | < 0.0005 | < 0.0005
| Barium (Ba) | 0.01 | mg/L | NV | 1 | <0.01 | <0.01 | <0.01 | 0.003 | 0.003 | 0.007 | 0.002 | 0.003 | 0.002 | 0.002 | 0.001
| Beryllium (Be) | 0.0005 | mg/L | NV | NV | <0.0005 | <0.0005 | <0.0005 | <0.002 | < 0.002 | <0.002 | <0.002 | <0.002 | < 0.002 | < 0.002 | < 0.002
| Boron (B) | 0.01/0.1 | mg/L | NV | 5 | <0.01 | <0.01 | <0.01 | <0.005 | < 0.005 | <0.005 | <0.005 | 0.007 | < 0.005 | < 0.005 | < 0.005
| Cadmium (Cd) | 0.0001 | mg/L | 1.7e-05 | 0.005 | <0.0001 | <0.0001 | <0.0001 | <0.005 | < 0.005 | <0.005 | <0.005 | <0.005 | < 0.005 | < 0.0001 | < 0.0001
| Calcium (Ca) | 1 | mg/L | NV | NV | 5 | 6 | 7 | 7.63 | 4.95 | 5.19 | 5.05 | 8 | 4.57 | 4.63 | 4.89
| Chromium (Cr) | 0.001 | mg/L | <0.01 | 0.05 | <0.001 | <0.001 | <0.001 | <0.002 | < 0.002 | <0.002 | <0.02 | 0.465 | < 0.002 | < 0.002 | < 0.002
| Cobalt (Co) | 0.0002 | mg/L | NV | NV | <0.0002 | <0.0002 | <0.0002 | <0.005 | < 0.005 | <0.005 | <0.005 | 0.012 | < 0.005 | < 0.005 | < 0.0005
| Copper (Cu) | 0.001 | mg/L | 0.002 | 1 (AO) | 0.003 | 0.002 | 0.001 | 0.004 | 0.009 | 0.004 | 0.004 | 0.01 | 0.01 | 0.0017 | < 0.002
| Iron (Fe) | 0.03 | mg/L | 0.3 | 0.3 (AO) | 0.05 | 0.06 | <0.03 | 0.035 | 0.166 | 0.24 | 0.085 | 3.44 | 0.101 | 0.066 | 0.028
| Lead (Pb) | 0.001 | mg/L | 0.001 | 0.01 | <0.001 | <0.001 | <0.001 | <0.02 | < 0.02 | <0.02 | <0.02 | <0.02 | < 0.02 | < 0.0001 | < 0.0001
| Magnesium (Mg) | 1 | mg/L | NV | NV | <1 | 1 | 1 | 1.63 | 0.94 | 1 | 0.99 | 1.56 | 0.86 | 0.88 | 0.94
| Manganese (Mn) | 0.01 | mg/L | NV | 0.05 (AO) | 0.02 | 0.02 | <0.01 | 0.025 | 0.13 | 0.102 | 0.08 | 0.064 | 0.029 | 0.018 | 0.012
| Molybdenum (Mo) | 0.005 | mg/L | 0.073 | NV | <0.005 | <0.005 | <0.005 | <0.01 | < 0.01 | <0.01 | <0.01 | 0.06 | < 0.01 | < 0.01 | < 0.0005
| Nickel (Ni) | 0.005 | mg/L | 0.025 | NV | <0.005 | <0.005 | <0.005 | <0.01 | < 0.01 | <0.01 | <0.01 | 0.54 | < 0.01 | < 0.01 | < 0.01
| Potassium (K) | 1 | mg/L | NV | NV | <1 | <1 | <1 | 0.2 | 0.1 | 0.2 | 0.1 | 0.2 | 0.2 | 0.2 | 0.1
| Selenium (Se) | 0.01 | mg/L | 0.001 | 0.01 | <0.001 | <0.001 | <0.001 | NA | NA | NA | NA | NA | NA | NA | NA
| Silicon (Si) | 0.1 | mg/L | NV | NV | 0.6 | 0.5 | 0.6 | 0.83 | 0.55 | 0.43 | 0.36 | 0.48 | 0.36 | 0.41 | 0.48
| Silver (Ag) | 0.0001 | mg/L | 0.0001 | NV | <0.0001 | <0.0001 | <0.0001 | <0.005 | <0.005 | <0.005 | <0.005 | <0.005 | < 0.005 | < 0.0001 | < 0.005
| Sodium (Na) | 2 | mg/L | NV | 200 (AO) | <2 | <2 | <2 | 1.2 | 0.8 | 1.1 | 0.8 | 1.5 | 0.9 | 0.7 | 0.7
| Strontium (Sr) | 0.001 | mg/L | NV | NV | 0.011 | 0.013 | 0.014 | 0.019 | 0.013 | 0.019 | 0.013 | 0.021 | 0.012 | 0.011 | 0.013
| Titanium (Ti) | 0.01 | mg/L | NV | NV | <0.01 | <0.01 | <0.01 | <0.005 | <0.005 | <0.005 | <0.005 | <0.005 | < 0.005 | < 0.005 | < 0.005
| Thallium (Tl) | 0.0001 | mg/L | 0.0008 | NV | <0.0001 | <0.0001 | <0.0001 | NA | NA | NA | NA | NA | NA | NA | NA
| Vanadiun (V) | 0.001 | mg/L | NV | NV | <0.001 | <0.001 | <0.001 | <0.005 | 0.005 | <0.005 | <0.005 | <0.005 | < 0.005 | < 0.005 | < 0.005
| Zinc (Zn) | 0.01 | mg/L | 0.03 | 5 (AO) | <0.01 | <0.01 | <0.01 | <0.005 | <0.005 | <0.005 | <0.05 | 0.011 | 0.021 | < 0.005 | < 0.005
Microbiology | Faecal Coliforms | 0 | ct/100mL | NV | 0 | NA | NA | 0 | <2 | 0 | <10 | <10 | <10 | 2 | 0 | 0
| Total Coliforms | 0 | ct/100mL | NV | 0 | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
Notes:
Bold | Exceeds CCME criteria
Shaded | Exceeds Guidelines for Canadian Drinking Water
NV | No value listed in criteria
NA | Not Analyzed/Not Applicable

## WWTP In (B)
Table 2: Influent Water Quality (WWTP)
Nunavut Water Board Licence 3AM-IQA0611 |  |  |  |  | Lab I.D. | 986494 | B13-22723-1 | B14-23243-1 | B-14-25349-1
City of Iqaluit |  |  |  |  | Sample Matrix | Wastewater | Wastewater | Wastewater | Wastewater
Sample Type
[5 empty] | Sampling Date | 2012-09-19 | 2013-08-27 | 29-Aug-14 | 2014-09-29
[5 empty] | Sample I.D. | Test B (WWTP In) | WTP Test B | Test B - WWTP Influent | Test B - WWTP
Group | Analyte | MRL | Units | CCME | Effluent Quality Criteria (Water Licence 3AM-IQA0611 )
|  |  |  | Water Quality Objectives | Wastewater Treatment Plant
General Chemistry and Nutrients | Nitrite (N-N02) | 0.1 | mg/L | 0.06 | NV | <0.1 | <0.1 | < 0.1 | < 0.1
| Nitrate (N-N03) | 0.1 | mg/L | 13 | NV | <0.1 | 0.1 | < 0.1 | < 0.1
| BOD5 | 1 | mg/L | NV | 30 (Avg), 45 (Max) | 212 | 169 | 186 | 143
| Ammonia (N-NH3) | 0.02 | mg/L | 0.019 | NV | 43.4 | 34.8 | 36.8 | 23.6
| Orthophosphate (O-P04) | 0.3 | mg/L | NV | NV | 14.1 | 3.89 | 4.24 | 2.52
| Total Phosphorus | 0.01 | mg/L | NV | NV | 7.63 | 11.9 | 5.39 | 4.64
Mercury | Mercury (Hg) | 0.0001 | mg/L | 2.6e-05 | NV | <0.0001 | NA | NA | NA
Metals | Aluminum (Al) | 0.01 | mg/L | 0.1 | NV | 0.8 | 0.68 | 0.78 | 0.36
| Antimony (Sb) | 0.0005 | mg/L | NV | NV | <0.01 | <0.0001 | 0.0008 | 0.0011
| Arsenic (As) | 0.01 | mg/L | 0.005 | NV | <0.05 | <0.0001 | 0.0009 | 0.0007
| Barium (Ba) | 0.01 | mg/L | NV | NV | <0.01 | 0.042 | 0.01 | 0.028
| Beryllium (Be) | 0.0005 | mg/L | NV | NV | <0.01 | <0.002 | < 0.002 | < 0.002
| Boron (B) | 0.01/0.1 | mg/L | NV | NV | <0.1 | 0.035 | 0.092 | 0.055
| Calcium (Ca) | 1 | mg/L | NV | NV | 25 | 30.9 | 21.6 | 20.1
| Cadmium (Cd) | 0.0001 | mg/L | 1.7e-05 | NV | <0.01 | <0.005 | < 0.005 | < 0.005
| Cobalt (Co) | 0.0002 | mg/L | NV | NV | <0.01 | <0.005 | < 0.005 | < 0.005
| Chromium (Cr) | 0.001 | mg/L | <0.01 | NV | <0.05 | 0.003 | < 0.002 | < 0.002
| Copper (Cu) | 0.001 | mg/L | 0.002 | NV | 0.38 | 0.393 | 0.157 | 0.221
| Iron (Fe) | 0.03 | mg/L | 0.3 | NV | 1.1 | 1.37 | 0.539 | 0.447
| Lead (Pb) | 0.001 | mg/L | 0.001 | NV | <0.01 | <0.02 | < 0.02 | < 0.02
| Magnesium (Mg) | 1 | mg/L | NV | NV | 4 | 4.6 | 4.31 | 3.66
| Manganese (Mn) | 0.01 | mg/L | NV | NV | 0.19 | 0.28 | 0.204 | 0.16
| Molybdenum (Mo) | 0.005 | mg/L | 0.073 | NV | <0.01 | <0..01 | < 0.01 | < 0.01
| Nickel (Ni) | 0.005 | mg/L | 0.025 | NV | <0.01 | 0.01 | < 0.01 | <0.01
| Potassium (K) | 1 | mg/L | NV | NV | 10 | 8.7 | 13 | 9
| Selenium (Se) | 0.01 | mg/L | 0.001 | NV | <0.05 | NA | NA | NA
| Silicon (Si) | 0.1 | mg/L | NV | NV | 1.6 | 1.77 | 2.17 | 1.4
| Silver (Ag) | 0.0001 | mg/L | 0.0001 | NV | <0.01 | <0.005 | < 0.005 | <0.005
| Sodium (Na) | 2 | mg/L | NV | NV | 21 | 20.7 | 30.1 | 20
| Strontium (Sr) | 0.001 | mg/L | NV | NV | 0.06 | 0.088 | 0.043 | 0.06
| Titanium (Ti) | 0.01 | mg/L | NV | NV | <0.1 | 0.01 | 0.01 | 0.006
| Thallium (Tl) | 0.0001 | mg/L | 0.0008 | NV | <0.01 | NA | NA | NA
| Vanadiun (V) | 0.001 | mg/L | NV | NV | <0.05 | <0.005 | < 0.005 | < 0.005
| Zinc (Zn) | 0.01 | mg/L | 0.03 | NV | 0.23 | 0.245 | 0.13 | 0.12
Microbiology | Faecal Coliforms | 0 | ct/100mL | NV | NV | 11200000 | 1700000 | 260000 | 4500000
| Total Coliforms | 0 | ct/100mL | NV | NV | 34700000 | 24000000 | 780000 | 53000000
Toxicity | Daphnia magna 48-hr LC50 | [5 empty] | Non-lethal | Non-lethal
| Rainbow Trout 96-hr single | [5 empty] | 100% Mortaility | 100% Mortaility
Notes:
Shaded | Exceeds Effluent Quality Criterion in Nunavut Water Board Licence 3AM-IQA0611
BOLD | Exceeds CCME criteria
NV | No value listed in criteria
NA | Not Analyzed

## WWTP Eff (C,D,E)
Table 3: Effluent Water Quality (WWTP)
Nunavut Water Board Licence 3AM-IQA0611 |  |  |  |  | Lab I.D. | 965782 | 974524 | 986499 | 1002735 | B13-04511-1 | B13-09349-1 | B13-15209-1 | B13-22724-1 | B13-29382-1 | B14-01871-1 | B14-01871-2 | B14-02458-1 | B14-09173-1 | B14-15362-1 | B14-23245-1 | B14-32434-1
City of Iqaluit |  |  |  |  | Sample Matrix | Wastewater | Wastewater | Wastewater | Wastewater | Wastewater | Wastewater | Wastewater | Wastewater | Wastewater | Wastewater | Wastewater | Wastewater | Wastewater | Wastewater | Wastewater | Wastewater
[5 empty] | Test | Test C | Test D | Test E | Test D | Test D | Test C | Test D | Test E | Test C | Test D | Test D | Test D | Test C | Test D | Test E | Test D
[5 empty] | Sampling Date | 2012-06-19 | 2012-07-25 | 2012-09-19 | 2012-12-05 | 2013-02-27 | 2013-04-23 | 2013-06-18 | 2013-08-27 | 2013-11-05 | 2013-12-17 | 2013-12-17 | 2014-02-04 | 2014-04-29 | 2014-06-24 | 29-Aug-14 | 16-Dec-14
[5 empty] | Sample I.D. | City of Iqaluit | WWTP Effluent | Test E (WWTP Eff) | Effluent WWTP | WWTP Eff-D | Y13-Test C-WWTP | Effluent Test D | WTP Test E | Test C | WWTP 1 Test D | WWTP 2 Test D |  |  |  | WWTP Effluent
Group | Analyte | MRL | Units | CCME | Effluent Quality Criteria (Water Licence 3AM-IQA0611 )
|  |  |  | Water Quality Objectives | Wastewater Treatment Plant
General Chemistry and Nutrients | BOD5 | 1 | mg/L | NV | 30 (Avg), 45 (Max) | 160 | 163 | 169 | 191 | 208 | 337 | 213 | 192 | 88 | 361 | 253 | 220 | 712 | 211 | 59 | 191
| Total Suspended Solids | 2 | mg/L | NV | 30 (Avg), 45 (Max) | NA | NA | NA | 135 | NA | 200 | 204 | 248 | 204 | 100 | 112 | 248 | 860 | 232 | 60 | 180
| Conductivity | 1 | umho/cm | NV | NV | 651 | 615 | 594 | NA | 531 | 620 | 625 | 483 | 484 | 546 | 549 | 485 | 433 | 504 | 525 | 480
| pH |  |  | 6.5 - 9 | 6 -9 | NA | NA | NA | NA | NA | 7.26 | 7.43 | 7.43 | 7.12 | 6.94 | 6.97 | 7.57 | 7.12 | 7.37 | 6.82 | 7.53
| Nitrite (N-N02) | 0.1 | mg/L | 0.06 | NV | <0.1 | <0.1 | <0.1 | <0.1 | <0.1 | <0.1 | <0.1 | <0.1 | <0.1 | <0.1 | <0.1 | < 0.1 | < 0.1 | <0.1 | < 0.1 | < 0.1
| Nitrate (N-N03) | 0.1 | mg/L | 13 | NV | <0.1 | <0.1 | <0.1 | <0.1 | <0.1 | 0.1 | 0.1 | 0.1 | 0.1 | <0.1 | <0.1 | < 0.1 | < 0.1 | 0.1 | < 0.1 | < 0.1
| Ammonia (N-NH3) | 0.02 | mg/L | 0.019 | NV | 49.1 | 42.9 | 42.8 | NA | 36.5 | 49.4 | 39.4 | 32.8 | 35.9 | 44 | 42.8 | 40.4 | 31.6 | 31.4 | 32.5 | 37.5
| Orthophosphate (O-P04) | 0.03 | mg/L | NV | NV | 14.6 | 11.7 | 13.8 | NA | 4.06 | 5.38 | 4.1 | 3.43 | 3.52 | 5.27 | 4.97 | 4.43 | 4.02 | 3.78 | 3.62 | 4.24
| Total Phosphorus | 0.01 | mg/L | NV | NV | 6.97 | 7.32 | 6.89 | NA | 7.64 | 10.3 | 7.53 | 5.95 | 6.44 | 8.15 | 8.3 | 7.84 | 9.36 | 6.4 | 5.07 | 6.12
Mercury | Mercury (Hg) | 0.0001 | mg/L | 2.6e-05 | NV | NA | <0.0001 | <0.0001 | <0.0001 | <0.00002 | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
Metals | Aluminum (Al) | 0.01 | mg/L | 0.1 | NV | NA | 0.8 | 0.5 | 0.7 | 0.44 | NA | 0.52 | 0.51 | NA | 0.42 | 0.38 | 0.47 | NA | 0.38 | 0.34 | 0.41
| Antimony (Sb) | 0.0005 | mg/L | NV | NV | NA | <0.01 | <0.01 | <0.01 | <0.0005 | NA | 0.001 | <0.0001 | NA | 0.0007 | <0.0005 | < 0.0005 | NA | 0.0008 | < 0.0005 | 0.0007
| Arsenic (As) | 0.01 | mg/L | 0.005 | NV | NA | <0.05 | <0.05 | <0.05 | 0.0006 | NA | 0.0006 | <0.0001 | NA | <0.0005 | <0.0005 | < 0.0005 | NA | <0.0005 | 0.0006 | 0.0008
| Barium (Ba) | 0.01 | mg/L | NV | NV | NA | 0.02 | <0.01 | <0.01 | 0.012 | NA | 0.026 | 0.04 | NA | 0.022 | 0.024 | 0.023 | NA | 0.03 | 0.008 | 0.013
| Beryllium (Be) | 0.0005 | mg/L | NV | NV | NA | <0.01 | <0.01 | <0.01 | <0.002 | NA | <0.002 | <0.002 | NA | <0.002 | <0.002 | < 0.002 | NA | <0.002 | < 0.002 | < 0.002
| Boron (B) | 0.01/0.1 | mg/L | NV | NV | NA | 0.1 | <0.1 | <0.1 | 0.05 | NA | 0.124 | 0.041 | NA | 0.052 | 0.048 | 0.041 | NA | 0.04 | 0.076 | 0.072
| Cadmium (Cd) | 0.0001 | mg/L | 1.7e-05 | NV | NA | <0.01 | <0.01 | <0.01 | <0.005 | NA | <0.005 | <0.005 | NA | <0.005 | <0.005 | < 0.005 | NA | <0.005 | < 0.005 | < 0.005
| Calcium (Ca) | 1 | mg/L | NV | NV | NA | 24 | 23 | 14 | 11.7 | NA | 20.4 | 24.8 | NA | 14.6 | 14.5 | 13.2 | NA | 22.5 | 19.2 | 12.7
| Chromium (Cr) | 0.001 | mg/L | 0.01 | NV | NA | <0.05 | <0.05 | <0.05 | 0.01 | NA | 0.003 | 0.002 | NA | <0.002 | <0.002 | < 0.002 | NA | 0.002 | < 0.002 | 0.003
| Cobalt (Co) | 0.0002 | mg/L | NV | NV | NA | <0.01 | <0.01 | <0.01 | <0.005 | NA | <0.005 | <0.005 | NA | <0.005 | <0.005 | < 0.005 | NA | <0.005 | < 0.005 | < 0.005
| Copper (Cu) | 0.001 | mg/L | 0.002 | NV | NA | 0.33 | 0.3 | 0.44 | 0.501 | NA | 0.44 | 0.366 | NA | 0.422 | 0.392 | 0.429 | NA | 0.379 | 0.213 | 0.416
| Iron (Fe) | 0.03 | mg/L | 0.3 | NV | NA | 0.7 | 0.6 | 0.4 | 0.413 | NA | 0.938 | 0.957 | NA | 0.584 | 0.528 | 0.655 | NA | 1.03 | 0.529 | 0.858
| Lead (Pb) | 0.001 | mg/L | 0.001 | NV | NA | <0.01 | <0.01 | <0.01 | <0.02 | NA | <0.02 | <0.02 | NA | <0.02 | <0.02 | < 0.02 | NA | <0.02 | < 0.02 | < 0.02
| Magnesium (Mg) | 1 | mg/L | NV | NV | NA | 11 | 4 | 3 | 3.16 | NA | 4.22 | 4.3 | NA | <0.01 | <0.01 | 3.17 | NA | 3.71 | 3.32 | 2.84
| Manganese (Mn) | 0.01 | mg/L | NV | NV | NA | 0.08 | 0.15 | 0.1 | 0.031 | NA | 0.11 | 0.212 | NA | 0.058 | 0.054 | 0.037 | NA | 0.065 | 0.134 | 0.047
| Molybdenum (Mo) | 0.005 | mg/L | 0.073 | NV | NA | <0.01 | <0.01 | <0.01 | <0.01 | NA | <0.01 | <0.01 | NA | <0.01 | <0.01 | < 0.01 | NA | <0.01 | < 0.01 | < 0.01
| Nickel (Ni) | 0.005 | mg/L | 0.025 | NV | NA | <0.01 | 0.01 | <0.01 | 0.02 | NA | <0.01 | <0.01 | NA | <0.01 | <0.01 | < 0.01 | NA | <0.01 | < 0.01 | < 0.01
| Potassium (K) | 1 | mg/L | NV | NV | NA | 16 | 9 | 10 | 11.3 | NA | 11.4 | 8.6 | NA | 10.6 | 10 | 9.5 | NA | 8.5 | 11 | 10
| Selenium (Se) | 0.01 | mg/L | 0.001 | NV | NA | <0.05 | <0.05 | <0.05 | <0.005 | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
| Silicon (Si) | 0.1 | mg/L | NV | NV | NA | 4 | 1.5 | 2.1 | 1.81 | NA | 2 | 1.6 | NA | 1.21 | 1.15 | 1.36 | NA | 1.11 | 1.51 | 1.24
| Silver (Ag) | 0.0001 | mg/L | 0.0001 | NV | NA | <0.01 | <0.01 | <0.01 | <0.005 | NA | <0.005 | <0.005 | NA | <0.005 | <0.005 | < 0.005 | NA | <0.005 | < 0.005 | < 0.005
| Sodium (Na) | 2 | mg/L | NV | NV | NA | 30 | 21 | 22 | 21.8 | NA | 25.5 | 21.2 | NA | 20.9 | 19.7 | 18.2 | NA | 24.8 | 27.3 | 22.1
| Strontium (Sr) | 0.001 | mg/L | NV | NV | NA | <0.05 | <0.05 | <0.05 | 0.029 | NA | 0.054 | 0.081 | NA | 0.048 | 0.05 | 0.044 | NA | 0.068 | 0.04 | 0.033
| Titanium (Ti) | 0.01 | mg/L | NV | NV | NA | <0.1 | <0.1 | <0.1 | 0.096 | NA | 0.013 | 0.011 | NA | 0.005 | <0.005 | < 0.005 | NA | 0.012 | < 0.005 | 0.007
| Thallium (Tl) | 0.0001 | mg/L | 0.0008 | NV | NA | <0.01 | <0.01 | <0.01 | <0.0003 | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
| Vanadiun (V) | 0.001 | mg/L | NV | NV | NA | <0.05 | <0.05 | <0.05 | <0.005 | NA | <0.005 | <0.005 | NA | <0.005 | <0.005 | < 0.005 | NA | <0.005 | < 0.005 | < 0.005
| Zinc (Zn) | 0.01 | mg/L | 0.03 | NV | NA | 0.18 | 0.14 | 0.2 | 0.177 | NA | 0.225 | 0.153 | NA | 0.196 | 0.176 | 0.194 | NA | 0.176 | 0.102 | 0.201
Microbiology | Faecal Coliforms | 0 | ct/100mL | NV | NV | 760000 | NA | 12800000 | 14300000 | 27000000 | 8800000 | 12100000 | 2000000 | 9200000 | 450000 | 340000 | 2200000 | 3000000 | 7300000 | 50000 | 6500000
| Total Coliforms | 0 | ct/100mL | NV | NV | 5300000 | NA | 36500000 | NA | 39000000 | 1250000 | 104000000 | 8000000 | >10000000 | 4500000 | 3700000 | 39000000 | 8500000 | 55000000 | 790000 | 46000000
Toxicity | Daphnia magna 48-hr LC50 | [11 empty] | Non-lethal | [6 empty] | Non-lethal
| Rainbow Trout 96-hr single | [11 empty] | 100% Mortaility | [6 empty] | Non-lethal
Notes:
BOLD | Exceeds CCME criteria
Shaded | Exceeds Effluent Quality Criterion in Nunavut Water Board Licence 3AM-IQA0611
NV | No value listed in criteria
NA | Not Analyzed

## sludge (F)
Table 4: Sludge Quality (WWTP)
Nunavut Water Board Licence 3AM-IQA0611 |  |  |  | Lab I.D. | 974526 | 986501 | 993791 | B13-15213-1 | B13-17499-1 | B13-22726-1 | B13-26564-1 | B14-15363-1 | B14-19764-1 | B14-23249-1
City of Iqaluit |  |  |  | Sample Matrix | Sludge | Sludge | Sludge | Sludge | Sludge | Sludge | Sludge | Sludge | Sludge | Sludge
Sample Type
|  |  |  | Sampling Date | 2012-07-25 | 2012-09-19 | 2012-10-25 | 2013-06-18 | 2013-07-08 | 2013-08-27 | 2013-10-07 | 2014-06-24 | 05-Aug-14 | 29-Aug-14
|  |  |  | Sample I.D. | Sludge | Test F (Sludge) | Sludge Sample | Sludge test F | Sludge Test F | Sludge Test F | Sludge Test F | Test F | Test F | Sludge Test F
Group | Analyte | MRL | Units | Northwest Territories Biosolids Criteria
General Chemistry and Nutrients | BOD5 | 1 | ug/g | NV | NA | NA | NA | >3000 | 33200 | 81800 | 244000 | 38400000 | 457000 | 628000
| pH | 1 |  | NV | 5.32 | 5.2 | 5.49 | 6.3 | 5.2 | 5.3 | 7.36 | 5.02 | 5.15 | 5.24
| Conductivity | 1 | umho/cm | NV | NA | NA | NA | 1480 | 644 | 1170 | 1940 | 1040 | 883 | 1550
| Moisture | 0.1 | % | NV | 76.4 | NA | 79.3 | 80.4 | 79.4 | 79.1 | 79.8 | 83.4 | 75.4 | 79.6
| Nitrite (N-N02) | 0.1 | ug/g | NV | <1.0 | <1.0 | <25 | 4 | 9 | 4 | <1 | 7 | 4 | 1
| Nitrate (N-N03) | 0.1 | ug/g | NV | <25 | <25 | <25 | 3 | 5 | 1 | 2 | 3 | 10 | 2
| Ammonia (N-NH3) | 0.02 | ug/g | NV | 1600 | 2200 | 1900 | 1370 | 769 | 2950 | 5050 | 1260 | 480 | 2640
| Orthophosphate |  | ug/g | NV | NA | NA | NA | 949 | 751 | 977 | 759 | 761 | 322 | 826
| Total Phosphorus | 0.01 | ug/g | NV | 2660 | 3670 | 2130 | 3690 | 3380 | 4850 | 3500 | 2800 | 3410 | 5860
Mercury | Mercury (Hg) | 0.0001 | ug/g | 5 | <0.1 | <0.1 | <0.1 | NA | NA | NA | NA | NA | NA | NA
Metals | Aluminum (Al) | 0.01 | ug/g | NV | 1190 | 633 | 950 | 950 | 660 | 3400 | 1940 | 1130 | 1040 | 660
| Antimony (Sb) | 0.0005 | ug/g | NV | <1 | <1 | <1 | 4 | <2 | <2 | <2 | <2 | < 2 | < 2
| Arsenic (As) | 0.01 | ug/g | 75 | <1 | <1 | <1 | <2 | <2 | 4 | <2 | <2 | < 2 | < 2
| Barium (Ba) | 0.01 | ug/g | NV | 17 | 13 | 11 | 19 | 16 | 31 | 29 | 23 | 28 | 14
| Beryllium (Be) | 0.0005 | ug/g | NV | <1 | <1 | <1 | <0.2 | <0.2 | <0.2 | <0.2 | <0.2 | < 0.2 | < 0.2
| Boron (B) | 0.01/0.1 | ug/g | NV | <5 | <10 | <10 | 4.8 | 2.4 | 6.2 | 3.3 | 5.1 | 4.6 | 6.1
| Cadmium (Cd) | 0.0001 | ug/g | 20 | <0.5 | <0.5 | <0.5 | <0.5 | <0.5 | <0.5 | <0.5 | 0.6 | < 0.5 | < 0.5
| Calcium (Ca) | 1 | ug/g | NV | 6700 | 5900 | 7900 | 11500 | 7910 | 10800 | 17700 | 18800 | 10900 | 9070
| Chromium (Cr) | 0.001 | ug/g | 1060 | 9 | 5 | 5 | 22 | 8 | 132 | 20 | 29 | 9 | 10
| Cobalt (Co) | 0.0002 | ug/g | 150 | <1 | <1 | <1 | 3 | <1 | 9 | 1 | 4 | < 1 | < 1
| Copper (Cu) | 0.001 | ug/g | 760 | 298 | 163 | 212 | 299 | 240 | 305 | 137 | 310 | 195 | 176
| Iron (Fe) | 0.03 | ug/g | NV | 4480 | 1190 | 3470 | 15400 | 1360 | 57200 | 6540 | 6320 | 10800 | 1710
| Lead (Pb) | 0.001 | ug/g | 500 | 13 | 3 | 6 | 6 | 7 | 32 | <5 | 15 | 8 | 5
| Magnesium (Mg) | 1 | ug/g | NV | 1200 | 700 | 700 | 1480 | 780 | 1890 | 1360 | 1320 | 1360 | 1110
| Manganese (Mn) | 0.01 | ug/g | NV | 54 | 41 | 59 | 127 | <1 | 292 | 116 | 57 | 79 | 61
| Molybdenum (Mo) | 0.005 | ug/g | 20 | 2 | <1 | <1 | 3 | <1 | 4 | 2 | 1 | 1 | 1
| Nickel (Ni) | 0.005 | ug/g | 180 | 6 | 3 | 4 | 16 | 7 | 347 | 12 | 14 | 6 | 8
| Potassium (K) | 1 | ug/g | NV | 800 | 700 | 700 | 990 | 1010 | 890 | 1420 | 1090 | 1100 | 920
| Silicon (Si) | 0.1 | ug/g | NV | 12 |  |  | 197 | 294 | 235 | 206 | 150 | 187 | 206
| Silver (Ag) | 0.0001 | ug/g | NV | 0.4 | 0.4 | 0.6 | 0.4 | 0.6 | 290 | 0.3 | 1.9 | < 0.2 | 0.3
| Sodium (Na) | 2 | ug/g | NV | 300 | 200 | 300 | 280 | 230 | 290 | 500 | 460 | 310 | 330
| Strontium (Sr) | 0.001 | ug/g | NV | <1 | 10 | 11 | 22 | 13 | 22 | 46 | 32 | 28 | 17
| Thallium (Tl) | 0.0001 | ug/g | NV | [8 empty] | NA | NA | bar: 2012-07-25 to 2014-06-24
| Vanadiun (V) | 0.001 | ug/g | NV | 5 | <2 | 3 | 7 | <1 | 19 | 4 | 3 | 3 | 1
| Zinc (Zn) | 0.01 | ug/g | 1850 | 296 | 157 | 159 | 163 | 228 | 221 | 147 | 368 | 169 | 204
Microbiology | Faecal Coliforms | 0 | ct/g | <1000 | NA | 37600000 | 3270000 | 960000 | 5200000 | 140000 | 100000 | 970000 | 47000000 | <100
| Total Coliforms | 0 | ct/g | NV | NA | 168000000 | 42300000 | 13400000 | 44000000 | 59000000 | 340000 | 12700000 | > 2000000000 | <100
Notes:
BOLD | Exceeds NWT criteria
NV | No value listed in criteria
NA | Not Analyzed

## landfill runoff (G)
Table 5: Effluent Water Quality
Nunavut Water Board Licence 3AM-IQA0611 |  |  |  |  | Lab I.D. | 973100 | 973099 | 973879 | B13-14900-1 | B13-17502-1 | B13-17502-2 | B14-15364-1 | B14-18517-1 | B14-21083-1
City of Iqaluit |  |  |  |  | Sample Matrix | Water | Water | Water | Water | Water | Water | Water | Water | Water
[5 empty] | Sample Type | Landfill Runoff | Landfill Runoff | Landfill Runoff | Landfill Runoff | Landfill Runoff | Landfill Runoff | Landfill Runoff | Landfill Runoff | Landfill Runoff
[5 empty] | Sampling Date | 2012-07-17 | 2012-07-18 | 2012-07-19 | 2013-06-17 | 2013-06-17 | 2013-06-17 | 2014-06-24 | 2014-07-23 | 15-Aug-14
[5 empty] | Sample I.D. | Retention Pond #1 | Retention Pond #2 | Retention Pond #3 | Retention Pond #1 | Retention Pond #2 | Detention #1 | Retention #2 | Retention Pond | Retention Pond (LRP-1)
Group | Analyte | MRL | Units | CCME | AECOM Report
|  |  |  | Water Quality Objectives | Surface Runoff
General Chemistry | pH | 1 |  | 6.5 - 9 | (6 - 9) | 8.26 | 8.27 | 8.31 | 7.7 | 7.91 | 7.67 | 7.77 | 8.07 | 8.24
| Total Suspended Solids | 2 | mg/L | NV | 180 | 16 | 17 | 10 | 12 | 12 | 52 | 32 | 20 | 29
| Turbidity | 0.1 | NTU | NV | NV | 10.5 | 8.9 | 8.2 | 63.4 | 68.7 | 225 | 63.8 | 40.7 | 44.1
| Total Organic Carbon (TOC) | 0.5 | mg/L | NV | NV | 20.3 | 23.1 | 20.7 | 22.1 | 41.1 | 40.3 | 35.1 | 7.9 | 39.3
Nutrients | Ammonia (N-NH3) | 0.02 | mg/L | 0.019 | NV | 4.9 | 4.49 | 4.39 | 3.77 | NA | NA | 9.45 | 9.1 | 8.9
| Total Kjeldahl Nitrogen | 0.1 | mg/L | NV | NV | 7.9 | 7.25 | 7.04 | 6.67 | 13.3 | NA | 13.8 | 14.3 | 13.2
| Total Phosphorus | 0.01 | mg/L | NV | NV | 0.05 | 0.05 | 0.03 | 0.1 | <0.01 | NA | 0.15 | 0.16 | 0.13
| BOD5 | 1 | mg/L | NV | 120 | 8 | 10 | 5 | 16 | 6 | 15 | 44 | 23 | 13
| COD | 5 | mg/L | NV | NV | 69 | 70 | 67 | 90 | 80 | 94 | 125 | 122 | 112
Mercury | Mercury (Hg) | 0.0001 | mg/L | 2.6e-05 | 0.0006 | <0.0001 | <0.0001 | <0.0001 | NA | NA | NA | 4e-05 | <0.00002 | < 0.00002
Metals | Aluminum (Al) | 0.01 | mg/L | 0.1 | 2 | 0.02 | 0.03 | 0.03 | 0.13 | 0.08 | NA | 0.38 | 0.05 | 0.02
| Antimony (Sb) | 0.0005 | mg/L | NV | NV | 0.0006 | 0.0007 | 0.0007 | 0.0021 | 0.002 | NA | 0.0029 | 0.0025 | 0.0011
| Arsenic (As) | 0.01 | mg/L | 0.005 | 0.1 | <0.01 | <0.01 | <0.01 | 0.0027 | 0.0048 | NA | 0.0065 | 0.0057 | 0.0082
| Barium (Ba) | 0.01 | mg/L | NV | 1 | 0.02 | 0.02 | 0.02 | 0.034 | 0.044 | NA | 0.042 | 0.044 | 0.046
| Beryllium (Be) | 0.0005 | mg/L | NV | NV | <0.0005 | <0.0005 | <0.0005 | <0.002 | <0.002 | NA | < 0.002 | <0.002 | < 0.002
| Boron (B) | 0.01/0.1 | mg/L | NV | 5 | 0.98 | 1.1 | 0.96 | 0.712 | 1.59 | NA | 1.54 | 1.73 | 1.84
| Cadmium (Cd) | 0.0001 | mg/L | 1.7e-05 | 10 | <0.0001 | <0.0001 | <0.0001 | <0.005 | <0.005 | NA | 0.00134 | <0.005 | < 0.005
| Calcium (Ca) | 1 | mg/L | NV | NV | 104 | 100 | 90 | 125 | 219 | NA | 155 | 177 | 196
| Chromium (Cr) | 0.001 | mg/L | <0.01 | 0.1 | 0.004 | 0.003 | 0.004 | <0.002 | <0.002 | NA | 0.002 | <0.002 | < 0.002
| Cobalt (Co) | 0.0002 | mg/L | NV | 0.5 | 0.0011 | 0.0011 | 0.0011 | <0.005 | 0.007 | NA | < 0.005 | <0.005 | < 0.005
| Copper (Cu) | 0.001 | mg/L | 0.002 | 0.2 | 0.006 | 0.006 | 0.006 | 0.026 | 0.018 | NA | 0.0346 | 0.016 | 0.005
| Iron (Fe) | 0.03 | mg/L | 0.3 | 0.3 | 1.26 | 1.14 | 1.23 | 5.88 | 5.61 | NA | 8.35 | 3.89 | 3.55
| Lead (Pb) | 0.001 | mg/L | 0.001 | NV | <0.001 | <0.001 | <0.001 | <0.02 | <0.02 | NA | 0.00613 | <0.02 | < 0.02
| Magnesium (Mg) | 1 | mg/L | NV | NV | 25 | 25 | 21 | 13.7 | 33.1 | NA | 35.1 | 37.7 | 40.2
| Manganese (Mn) | 0.01 | mg/L | NV | 0.05 | 0.46 | 0.39 | 0.41 | 2.38 | 3.17 | NA | 1.41 | 1.96 | 1.86
| Molybdenum (Mo) | 0.005 | mg/L | 0.073 | 0.2 | <0.005 | <0.005 | <0.005 | <0.01 | <0.01 | NA | < 0.01 | <0.01 | < 0.01
| Nickel (Ni) | 0.005 | mg/L | 0.025 | 0.3 | 0.011 | 0.011 | 0.011 | 0.01 | 0.01 | NA | 0.0187 | 0.02 | 0.02
| Potassium (K) | 1 | mg/L | NV | NV | 32 | 100 | 30 | 14 | NA | NA | 42.8 | 45.5 | 51
| Silicon (Si) | 0.1 | mg/L | NV | NV | 2 | 2 | 1.8 | 2.18 | 3.2 | NA | 3.4 | 3.19 | 4.24
| Silver (Ag) | 0.0001 | mg/L | 0.0001 | 0.1 | <0.0001 | <0.0001 | <0.0001 | <0.005 | <0.005 | NA | < 0.005 | <0.005 | < 0.005
| Strontium (Sr) | 0.001 | mg/L | NV | NV | 0.554 | 0.567 | 0.594 | 0.462 | 1.05 | NA | 0.819 | 0.931 | 1.01
| Sodium (Na) | 2 | mg/L | NV | NV | 186 | 181 | 153 | 54.3 | 181 | NA | 210 | 205 | 241
| Titanium (Ti) | 0.01 | mg/L | NV | NV | <0.01 | <0.01 | <0.01 | <0.005 | <0.005 | NA | 0.018 | <0.005 | < 0.005
| Thallium (Tl) | 0.0001 | mg/L | 0.0008 | NV | <0.0001 | <0.0001 | <0.0001 | NA | NA | NA | NA | NA | NA
| Vanadiun (V) | 0.001 | mg/L | NV | NV | 0.002 | 0.002 | 0.002 | <0.005 | 0.005 | NA | < 0.005 | <0.005 | < 0.005
| Zinc (Zn) | 0.01 | mg/L | 0.03 | 0.5 | 0.24 | 0.2 | 0.19 | 5.22 | 4.39 | NA | 2.99 | 2.27 | 0.848
PCBs | Polychlorinated Biphenyls (PCBs) | 0.1 | µg/L | 0.001 | 1 | <0.1 | <0.1 | <0.1 | <0.05 | <0.05 | NA | < 2 | <0.4 | < 0.05
VOC Surrogates | Toluene-d8 | 1 | % | NV | NV | 92 | 93 | 97 | NA | 98.8 | NA | 91.9 | 99.3 | 94.4
VOCs | Benzene | 0.5 | µg/L | 370 | 0.37 | <0.5 | <0.5 | <0.5 | <0.5 | <0.5 | NA | 1.7 | <0.5 | < 0.5
| Ethylbenzene | 0.5 | µg/L | 90 | 0.09 | <0.5 | <0.5 | <0.5 | <0.5 | <0.5 | NA | < 0.5 | <0.5 | < 0.5
| m/p-xylene | 0.5 | µg/L | NV | NV | <0.5 | <0.5 | <0.5 | <1.0 | <0.5 | NA | < 0.4 | <0.4 | < 0.4
| o-xylene | 0.5 | µg/L | NV | NV | <0.5 | <0.5 | <0.5 | <0.5 | <0.5 | NA | < 0.1 | 0.2 | < 0.1
| Toluene | 0.5 | µg/L | 2 | 0.002 | <0.5 | <0.5 | <0.5 | 0.7 | <0.5 | NA | < 0.5 | <0.5 | < 0.5
Microbiology | Faecal Coliforms | 0 | ct/100mL | NV | NV | <10 | <10 | 0 | 20 | 20 | NA | <10 | <10 | <10
| Total Coliforms | 0 | ct/100mL | NV | NV | 70 | 200 | 63 | 5700 | 200 | NA | 40 | 200 | 160
Notes:
Shaded | Exceeds AECOM criteria
BOLD | Exceeds CCME criteria
NV | No value listed in criteria
NTU | Nephelometric turbidity units
NA | Not Analyzed

## sewage lagoon
Table 1: Effluent Water Quality (Sewage Lagoon Effluent)
Nunavut Water Board Licence 3AM-IQA0611
City of Iqaluit |  |  |  | Lab I.D. | B13-15122-1
|  |  |  | Sample Matrix | Water
Test
|  |  |  | Sampling Date | 2013-06-18
|  |  |  | Sample I.D. | Sewage Effluent
Analyte | MRL | Units | CCME | Effluent Quality Criteria (Water Licence 3AM-IQA0611 )
|  |  | Water Quality Objectives | Wastewater Treatment Plant
BOD5 | 1 | mg/L | NV | 120 (Avg), 180 (Max) | 26
Oil and Grease |  | mg/L |  | no sheen | <1
Total Suspended Solids | 2 | mg/L | NV | 180 (Avg), 270 (Max) | 20
pH |  |  | 6.5 - 9 | 6 -9 | 6.96
Notes:
Shaded | Exceeds Effluent Quality Criterion in Nunavut Water Board Licence 3AM-IQA0611
NV | No value listed in criteria