Monthly General Monitoring Report – June 2014

Nunavut Water Board Submission

Type of Document

Final

Project Name

Monthly General Monitoring Report – June 2014

Water License Monitoring Program

Iqaluit, Nunavut

Licence

3AM-IQA0611

Prepared By:  Robert Renaud

exp Services Inc.

100-2650 Queensview Drive

Ottawa, Ontario  K2B 8H6

Canada

Reviewed By: Paul Clow

City of Iqaluit

PO Box 460

Iqaluit, NU, X0A 0H0

Canada

Date Submitted

September 5, 2014

Monthly General Monitoring Report – June 2014

Nunavut Water Board Submission

Type of Document:

Final

Project Name:

Monthly General Monitoring Report – June 2014

Water Licence Monitoring Program

Iqaluit, Nunavut

Licence:

3AM-IQA0611

Prepared By:	Reviewed By:

exp Services Inc.	City of Iqaluit

100-2650 Queensview Drive	PO Box 460

Ottawa, Ontario  K2B 8H6	Iqaluit, NU, X0A 0H0

Canada	Canada

T:  613-688-1899	T:  867.979.5600

F:  613-225-7337  	F:  867.979.5922

www.exp.com	www.city.iqaluit.nu.ca

_______________________________________	____________________________________

| Robert Renaud, M.Sc., P.Geo. (NU, NT) Practice Lead – Northern Environmental Services Earth & Environment | Paul Clow Project Officer Engineering and Sustainability |
| --- | --- |

Date Submitted:

September 5, 2014

# Executive Summary

As a condition of Nunavut Water Board (NWB) Licence 3AM-IQA0611, the City of Iqaluit (City) is required to submit a monthly general monitoring report to the Nunavut Water Board (NWB).

The objective of this monthly general monitoring report is to document the environmental monitoring, pursuant to the NWB Licence 3AM-IQA0611, undertaken by the City during the month.  This monthly general monitoring report includes a description of the sampling locations, the test group parameters, all laboratory analytical data and an evaluation of compliance with the NWB licence conditions.

This report presents the results of the samples collected from the West 40 Landfill Retention Pond decant, the Water Treatment Plant, the Wastewater Treatment Plant (effluent), and Sewage Sludge on June 24, 2014.

- Based on the results of the environmental monitoring program for the month of June 2014, the following conclusions are provided:

Parameters in the raw water entering the WTP were within the Canadian Drinking Water Standards (criteria).

The City’s primary wastewater treatment system is able to provide some reduction in BOD and TSS levels in the effluent, but cannot achieve the criteria in the City’s Water Licence.

The upgrade of the WWTP to a secondary treatment facility is needed to achieve the effluent criteria in the City’s Water Licence.

Parameters measured in the June 24, 2014 sludge sample met criteria with the exception of faecal coliforms.

The continued exceedances of the CCME and AECOM surface water criteria from the landfill runoff pose a concern for the environment.

Table of Contents

Executive Summary	EX-i

1	Introduction	1

1.1	Site Description	1

1.2	Project Objectives	2

1.3	Scope of Work	2

2	Methodology	3

2.1	Environmental Monitoring Sample Collection Program	3

2.1.1	Water Quality Parameters	3

2.1.2	Sampling Locations	3

2.1.3	Laboratory Submission	4

3	Effluent Quality Assessment	5

3.1	Assessment Criteria	5

3.2	Analytical Results	5

3.2.1	Station IQA-01 (Influent to the Water Treatment Plant)	5

3.2.2	Station IQA-04 (Effluent from the Wastewater Treatment Plant)	5

3.2.3	Station IQA-06 (Sludge from the Wastewater Treatment Plant)	5

3.2.4	Station IQA-08 (Landfill Retention Pond)	5

3.3	Discussion	6

3.3.1	Station IQA-01 (Influent to the Water Treatment Plant)	6

3.3.2	Station IQA-04 (Effluent from the Wastewater Treatment Plant)	6

3.3.3	Station IQA-06 (Sludge from the Wastewater Treatment Plant)	6

3.3.4	Station IQA-08 (Landfill Retention Pond)	6

4	Conclusions	7

5	References	8

6	Limitations	9

Appendices

Appendix A:   Figures

Appendix B:   Current Monitoring Program Test Dates

Appendix C:   Analytical Summary Tables

Appendix D:   Laboratory Certificates of Analysis

Appendix E:   City of Iqaluit’s Water Licence

# Introduction

As a condition of Nunavut Water Board (NWB) Licence 3AM-IQA0611, the City of Iqaluit (City) is required to submit a Monthly General Monitoring Report to the Nunavut Water Board (NWB).

## Site Description

The City of Iqaluit overlooks Koojesse Inlet on the south coast of Baffin Island (Figure 1, Appendix A).  Lake Geraldine supplies raw water to the City.  During the spring and summer, runoff from the surrounding watershed fills the lake.  Water is stored for over-winter consumption by a dam on Lake Geraldine.  From the dam outfall, water is transmitted by gravity to the water treatment plant (WTP) where it is treated by UV, filtration, chlorination, and fluorination.  Treated water is stored in two storage reservoirs located next to the WTP prior to entering the main distribution system (see Figure 2, Appendix A).

The City's wastewater receives primary treatment at the wastewater treatment plant (WWTP) before being disposed in Frobisher Bay (Figure 3, Appendix A).  The sewage lagoon is used as a backup facility only.

Landfill runoff is collected in the on-site detention ponds.  The run-off is then pumped to the retention pond located across the road from the landfill (Figure 4, Appendix A).  When the retention pond is decanted, a 4" pump is then connected to a Geotube dewatering bag and the retention pond is decanted through the Geotube.

The water licence issued to the City (3AM-IQA0611) by the NWB specifies nine monitoring stations across the licensed facilities (the WTP, WWTP), and West 40 Landfill).

- Station IQA-01 is a raw water supply (from Lake Geraldine) sampling location, prior to treatment at the WTP;

- Station IQA-02 is a wastewater sampling location at the final discharge point from the sewage lagoon;

- Station IQA-03 is a wastewater sampling location of the influent to the sewage lagoon;

- Station IQA-04 is a wastewater sampling location at the final discharge point from the WWTP;

- Station IQA-05 is a wastewater sampling location of the influent to the WWTP;

- Station IQA-06 is a sample of sludge from the WWTP;

- Station IQA-07 is a sample of surface water entering the West 40 Landfill site;

- Station IQA-08 is a sample of surface water from the final discharge point from the West 40 Landfill site, and,

- Station IQA-09 is a sample of contaminated soil accepted at the West 40 Landfill site.

It should be noted that the landfill does not accept contaminated soil; therefore, Station IQA-09 is inactive.  Station IQA-07 is also inactive because berms prevent surface water from entering the West 40 Landfill.

## Project Objectives

The objective of this monthly general monitoring report is to document the environmental monitoring, pursuant to the NWB Licence 3AM-IQA0611 (see Appendix E), undertaken by the City during the month.  This monthly general monitoring report includes a description of the sampling locations, the test group parameters, all laboratory analytical data and an evaluation of compliance with the NWB licence conditions.

## Scope of Work

The environmental monitoring program consisted of the following general tasks:

Completion of environmental sampling and laboratory submission; and,

Data compilation, interpretation and reporting.

# Methodology

## Environmental Monitoring Sample Collection Program

### Water Quality Parameters

The City’s NWB-issued licence (3AM-IQA0611) specifies which water quality parameters must be measured and in what frequency they must be measured during the environmental monitoring program.

Table 1 of Schedule C of the Water Licence 3AM-IQA0611 identifies the various groups of analytical parameters that must be measured for the various sample types (e.g., routine, influent, effluent, potable water, etc.).  Table 2 of Schedule C of the water licence specifies the analytical test groups, frequency of sampling and responsible party for each of the monitoring stations.

The City developed a sampling schedule to meet these monitoring requirements (see Appendix B for schedule used).  Samples at IQA-08 and IQA-02 are to be completed during decants and were not specifically scheduled.

This report outlines the results of the analytical testing on the samples taken on June 24, 2014, which included the following test groups:

- Test A – Influent to the Water Treatment Plant (Station IQA-01);

- Test D – Effluent from the Wastewater Treatment Plant (Station IQA-04);

- Test F – Sludge from the Wastewater Treatment Plant (Station IQA-06); and,

- Test G – Final discharge point from the West 40 Landfill (Station IQA-08).

### Sampling Locations

The following table includes the Station IDs, description and the geographic coordinates for the five monitoring stations sampled during the month of June 2014.

Table 1 –Geographic Coordinates for the Monitoring Stations for NWB Licence 3AM-IQA0611

| Station ID | Description | Latitude* | Longitude* |
| --- | --- | --- | --- |
| IQA-01 | Influent to the Water Treatment Plant | 63°45’12’’ N | 68°30’22’’ W |
| IQA-04 | Effluent from the Wastewater Treatment Plant | 63°44’43’’ N | 68°32’20’’ W |
| IQA-06 | Sludge from the Wastewater Treatment Plant | 63°44’45’’ N | 68°32’20’’ W |
| IQA-08 | Retention Pond at the Landfill | 63°43’47’’ N | 68°32’11’’ W |

* NAD 83

Refer to the “City of Iqaluit - Quality Assurance / Quality Control Plan”, prepared by exp Services Inc., and dated February 2013, for additional details regarding the locations of the sampling points.

### Laboratory Submission

All environmental monitoring samples were submitted to Caduceon Environmental Laboratories, a CALA accredited laboratory for analysis of the parameters listed in Section 2.1.1 (above).  A quality assurance (QA) and quality control (QC) program was also implemented to ensure that the analytical results received are accurate and dependable.  A QA/QC program is a system of documented checks that validate the reliability of the data collected regarding any given site.  Quality Assurance is a system that ensures that quality control procedures are correctly performed and documented.  Quality Control refers to the established procedures observed both in the field and in the laboratory, designed to ensure that the resulting end data meet intended quality objectives.  The QA/QC program incorporated the following components:

Prevention of cross-contamination;

Sampling containers, preservation and hold times;

Sampling, packaging and transport;

Sample identification requirements;

Chain of custody;

Sample transmittal documentation;

Initial check of samples and documentation; and,

Verification of the integrity and condition of all sample coolers.

# Effluent Quality Assessment

## Assessment Criteria

The results for the influent to the Water Treatment Plant samples were compared to the Canadian Drinking Water Quality Objectives (CDWG).  The assessment of sludge was compared to criteria utilized by the Northwest Territories from the document entitled A Review of the Current Canadian Legislative Framework for Wastewater Biosolids (CCME, 2010).

## Analytical Results

A summary of the analytical results obtained from previous environmental monitoring and the current monitoring program is presented in Appendix C, along with the applicable assessment criteria.  The laboratory Certificates of Analysis from the current round of sampling are presented in Appendix D.

### Station IQA-01 (Influent to the Water Treatment Plant)

Based on the analytical results obtained for the June 24, 2014 WTP influent samples, three exceedances of the Canadian Drinking Water Guidelines were measured, including chromium, iron, and manganese.  Faecal coliforms were not detected in the raw water stream.

### Station IQA-04 (Effluent from the Wastewater Treatment Plant)

Based on the analytical results obtained for the monitoring event for the June 24, 2014 WWTP effluent samples, BOD and TSS exceeded the effluent criteria stipulated by the water licence.  Ammonia, aluminum, copper and iron were elevated above the CCME criteria.  These exceedances represent a concern.

### Station IQA-06 (Sludge from the Wastewater Treatment Plant)

Based on the analytical results obtained for June 24, 2014 sewage sludge sample, one exceedance of the Northwest Territories Biosolids criteria was measured.  Faecal coliforms were significantly elevated above the NWT criteria for biosolids.  Where values for metals exist with the NWT biosolids criteria, the measured concentrations of metals in the sludge sample were far below the required criteria.

### Station IQA-08 (Landfill Retention Pond)

Based on the analytical results obtained for June 24, 2014 landfill retention pond sample iron, manganese, zinc and toluene were measured above the AECOM criteria.  In addition, ammonia, cadmium, copper, iron, mercury, and zinc were measured above the CCME criteria.

## Discussion

### Station IQA-01 (Influent to the Water Treatment Plant)

Three exceedances of the Canadian Drinking Water Guidelines were measured, including chromium, iron, and manganese.  The measured manganese concentration slightly exceeded the CDWG (aesthetic) objective.  The concentrations of the other measured parameters are comparable to what has been measured in previous sampling rounds.  A second water sample of raw water from Lake Geraldine (at Station IQA-01) was collected the same day for laboratory analyses of an extended suite of parameters.  The purpose of this second sample was to determine if the on-going landfill fire had impacted the raw water source.  The measured concentration of chromium in the second sample was than the MDL (i.e., <0.002 mg/L).  As such, chromium in the raw water is not considered to be problematic.  Iron was not measured in the sample collected for the examination of impacts from the landfill fire.  However, the measured concentration of iron in the water licence monitoring program sample was 3.44 mg/L.  This exceeded the CDWG (aesthetic) objective of 0.30 mg/L.  It should be noted that iron concentrations up to 10 mg/L are considered treatable, so this raw water iron concentration is not significant.  Overall, there are no concerns associated with this water stream.

### Station IQA-04 (Effluent from the Wastewater Treatment Plant)

The exceedances for BOD and TSS above the water licence criteria, as well as ammonia and several metals above CCME criteria represent a concern as this water is being discharged into the environment.  It was not possible to evaluate the effectiveness of treatment as no influent WWTP sample was collected.

The elevated readings are consistent with what was measured in numerous previous sampling rounds.  Since the wastewater treatment plant provides primary treatment only, it is not possible to achieve the effluent quality criteria specified in the water licence without a secondary treatment process.

The City is currently planning on upgrading the WWTP to a secondary treatment facility to meet the effluent criteria set out in its Water Licence.  Design and planning work is expected to start in 2014 and the upgrades are expected to be complete by the end of 2018.

### Station IQA-06 (Sludge from the Wastewater Treatment Plant)

Parameters generally met criteria with the exception of faecal coliforms.  The measured faecal coliforms concentrations in the sewage sludge have been consistently elevated in all monitoring program samples for which this parameter was measured.  In 2009, the City completed a study which showed that the sludge can be effectively treated through a freeze-thaw dewatering and compost process at the landfill.

### Station IQA-08 (Landfill Retention Pond)

The exceedances in the landfill retention pond represent a concern if being discharged into the environment directly.  However, the TSS is effectively reduced through the use of the Geotube bag during the decant.

# Conclusions

- Based on the results of the environmental monitoring program for the month of June, 2014, the following conclusions are provided:

Parameters in the raw water entering the WTP were within the Canadian Drinking Water Standards (criteria).

The City’s primary wastewater treatment system is able to provide some reduction in BOD and TSS levels in the effluent, but cannot achieve the criteria in the City’s Water Licence.

The upgrade of the WWTP to a secondary treatment facility is needed to achieve the effluent criteria in the City’s Water Licence.

Parameters measured in the June 18, 2013 sludge sample met criteria with the exception of faecal coliforms.

The continued exceedances of the CCME and AECOM surface water criteria from the landfill runoff pose a concern for the environment.

# References

- AECOM, City of Iqaluit West 40 Landfill Drainage Management Review, Project Number 60221928, October 16, 2011.

- AECOM, Iqaluit Sewage Sludge Management Composting Pilot Project Report, Project Number 106787-03, March 31, 2009.

- Canadian Council of Ministers of the Environment (CCME), Canadian Water Quality Guidelines for the Protection of Aquatic Life, 1999.

- Canadian Council of Ministers of the Environment (CCME), A Review of the Current Canadian Legislative Framework for Wastewater Biosolids, 2010.

- Exp Services Inc., City of Iqaluit - Quality Assurance / Quality Control Plan, February 2013.

- Health Canada, Guidelines for Canadian Drinking Water Quality, 2013.

- Nunavut Water Board Licence (3AM-IQA0611), Issued May 15, 2006.

# Limitations

This report has been prepared for and is intended for the exclusive use of the Nunavut Water Board.  The contents of this report should not be relied upon by any other party without the expressed written consent of the City of Iqaluit.  The findings are considered to be representative of site conditions at the time of environmental monitoring.

We trust this report is satisfactory for your purposes.  If you have any questions regarding our submission, please do not hesitate to contact this office.

Appendix A:  
Figures

Appendix B:  
Current Monitoring Program Test Dates

Appendix C:  
Analytical Summary Tables

Appendix D:  
Laboratory Certificates of Analysis

Appendix E:  
City of Iqaluit’s Water Licence