1+1

Environment and Climate Change Canada

Environnement et

Changement climatique Canada

Environmental Protection Operations Directorate (EPOD) Prairie & Northern Region (PNR)

5019 52nd Street, 4th Floor

P.O. Box 2310

Yellowknife, NT X1A 2P7 June 6, 2017

ECCC File: 6200 000 016/004 NWB File: 3BM-PAN1417

Karen Kharatyan

Acting Manager of Licensing Nunavut Water Board

  - Box 119

Gjoa Haven, NU XOB 1JO

via email: licensing@nwb-oen.ca

RE: 3BM-PAN1417 - Hamlet of Pangnirtung -Water Licence Renewal Amendment Attention: Karen Kharatyan

Environment and Climate Change Canada (ECCC) has reviewed the information submitted to the Nunavut Water Board regarding the above-mentioned water licence renewal amendment application and is submitting comments via email. ECCC's specialist advice is provided based on our mandate, in the context of the Canadian Environmental Protection Act, the pollution prevention provisions of the Fisheries Act, the Migratory Birds Convention Act, and the Species at Risk Act.

The following comments are provided:

    - ECCC recommends that the Type A Water Licence include a condition requiring that acute lethality testing be undertaken at end of pipe for the Pangnirtung Waste Water Treatment Plant. Given that the plant is treating fish processing plant wastewater as well as domestic wastewater there are additional contaminants associated with the cleaning chemicals that enter the treatment system. These chemicals have the potential to reduce the effectiveness of the water treatment plant by impacting the bacteria that are required to treat the wastewater. This has the potential to lead to increased concentrations of parameters of concern associated with the domestic wastewater being released into the receiving environment. This testing will help to inform the  Board of treatment efficacy.

Ans.: While it is true there are “cleaning chemicals” used  at the Fish plant, in conversations with plant management, the quantity used is small and the composition is acceptable for receiving at the Waste water Treatment Plant (WWTP). Under normal operation at the Fish plant, no negative impacts have been experienced at the WWTP. The WWTP operations personnel have been directed to record the trucks that are delivering fish plant process wastewater to the WWTP. Acute  toxicity testing can be added to the testing for final effluent once it is included in the new licence.

    - There are no figures provided to indicate the path of the effluent from the water

Treatment plant to Pangnirtung Fiord and the point of discharge. ECCC recommends that Figures/maps be provided.

Ans.:  Refer to the attached Figure/drawing showing the riprap route for the final effluent to the fiord.

    - The Pangnirtung Wastewater Treatment Facility Upgrade Process Operation Manual provides information on how the WWTP functions; however, specific details on output effluent quality are not included in the submission. ECCC recommends that a summary of effluent quality during sampling events since the implementation of the waste water treatment plant be provided.

Ans.: In Plant testing is done frequently and an excel spread sheet is attached. The effluent samples are also tested in the accredited Caduecon Lab in Ottawa and the test results are attached.

    - It is stated in the Solid Waste Operation and Maintenance Plan that the leachate from the solid waste disposal facility enters the sewage treatment wetland. This sewage treatment wetland is not discussed anywhere else in the application, nor is it depicted in any of the figures. ECCC recommends that the Proponent provide clarification on how the leachate is collected from the solid waste operation, how the leachate is managed after collection, if/where it is discharged to the environment, and provide information on the quality of the leachate that is being produced, and that is ultimately entering the receiving environment.

Ans.: The Leachate from Landfill site and metal sites are naturally treated in the wetland. The past lab results are attached. The monitoring stations are established and sampling will be continued at those stations in each summer.

The effluent quality at end of the sewer pipe needs to satisfy the water licence compliancy. The effluent outfalls on gravel pad prior to running to the sea. The past in Plant lab test results and the Caduecon  lab results of the effluent are attached.

The sketches attached show the relative locations of the Environmental facilities and wetlands including monitoring stations.

    - The Solid Waste Operation and Maintenance Plan does not discuss all leachate/run-off monitoring that is required under the existing water license. PAN-

3 (effluent discharge), PAN-4  (leachate from sludge dumping), and PAN-5 (leachate from domestic waste dumping) are listed, but the plan does not discuss the required sampling at PAN-6 (run-off from the metals storage are). In addition , the frequency of sampling is not provided for PAN-5 (Section 8.1 - Table 7). ECCC recommends that the Solid Waste Operations and Maintenance Plan be updated to ensure consistency with license conditions.

Ans.: The Solid waste management O&M Manual has been updated (2nd Revision) in June 2017 to satisfy this item and attached.

Should  you  require  further  information,  please  do  not  hesitate  to  contact  me  at (867)669-4732 or Emily.Nichol@canada.ca

Sincerely,

Emily Nichol

Environmental Assessment Coordinator

cc:		Bradley Summerfield, Senior Environmental Assessment Coordinator Georgina Williston, Head, Environmental Assessment North (NT and NU), PNR-EPOD

2