## Slide 1
Intake rest at this location
Bed level of the river
Water flows
Towards the sea
Duval River
Intake
Note: This is the normal practice of the intake location for the stream flow from where water is being extracted. Hamlet of Pangnirtung extracts water mostly in August. In the attached spread sheet, the minimum discharge is shown 0.785 m3/s (785L/s) in 1981. Discharge might be varied due to the annual snow fall and climate change. No record is available since 1984. Hamlet uses a pump 31.67L/s capacity whereas the instantaneous flow was minimum 785L/s in August 1981 . Therefore we could easily consider that extraction rate is less than 10% of the minimum instantaneous flow rate ( 10% of 785L/s= 78.5L/s). This operation is considered safe and no impact to the River flow)
A
A
Section – A-A