# List of Commitments Resulting from Technical Meeting for Water Licence No. 3AM-PAN---- Renewal Application

| No. | Party Responsible for Commitment | Party(s) who raised (Item#) | Issue - TM Commitment | Timeline for Submission | Form of Submission | Actual Submission date |
| --- | --- | --- | --- | --- | --- | --- |
|  | GN-CGS | DFO ECCC | To provide updated assessment of pumping that demonstrates that the 10% of instantaneous flow is maintained (compared to the 10% of average mean flow that was previously provided) | Dec.31,2017 | Updated assessment document | Dec.20,2017 |
|  | GN-CGS | ECCC INAC | Update to Operations & Maintenance Manual for Solid Waste Facilities | December 21, 2017 | Updated O&M Manual to include various updates, including the addition of a new Chapter to include a Drainage Management Plan | Dec.20,2017 |
|  | GN-CGS | ECCC INAC | Update to Operations & Maintenance Manual for Water Supply Facilities to add Truck Fill Station | Dec.31,2017 | Updated O&M Manual | Dec.20,2017 |
|  | GN-CGS | INAC NWB | GN-CGS to retain consultant to conduct study: discharge volume; velocity; erosion and sedimentation; Hydraulics; hydrology, water quality and thermal erosion of the Duval River. | Within 4 yrs. from the date of the Licence is issued. | Consultant’s Report on Hydrology for the Duval River | Waiting for the new license |
|  | GN-CGS | INAC | To provide pictures, engineering drawings and/or plans associated with the reservoir berm rehabilitation work that took place in 2017 | Dec.31,2017 |  |  |
|  | GN-CGS | NWB | The request was for topographical information regarding all facilities. Topographical maps should be included with all plans, reasonable scale to include site facilities, water bodies, direction of flow (gradient, i.e. 1m contour lines), etc. | Dec.31,2017 | Update of management plans to include appropriate mapping, Spill Contingency Plan, O&M manuals where appropriate | Topo information is not available right now. These Maps will be submitted within 2yrs from the date of the licence renewal |
|  | GN-CGS | INAC | GN-CGS commitment was to add direction of water flows and co-ordinates of sampling points to current pictures of facilities | Dec.31,2017 | Update pictures with this additional information | The Drainage flow Maps will be developed as soon as the item 6 is complete in next 2 yrs. from the date of the licence renewal. |
|  | GN-CGS | ECCC NWB | QA/QC Plan for water sampling under the Licence | Dec.31,2017 | QA/QC Plan for water sampling filed with the NWB | Dec.20,2017 |
|  | GN-CGS | DFO | To confirm the design/criteria used for the water intake/screen and compare to DFO guideline documents | Dec.,2017 | Correspondence from GN-CGS to DFO (filed with the NWB) providing additional information | Dec. 20,2017 |