                                                ANNUAL REPORT 






FOR THE HAMLET OF PANGNIRTUNG, 2018


YEAR BEING REPORTED:  2018


The following information is compiled pursuant to the requirements of Part B, Item 1 of Water Licence # 3BM-PAN1417issued to the Hamlet of Pangnirtung.
i) - iii)
tabular summaries of all data generated under the “Monitoring Program”; monthly and annual quantities in cubic metres of freshwater obtained from all sources; monthly and annual quantities in cubic metres of each and all wastes discharged;

Attached are quantities of water used as reported in our On Tap Water Delivery System and the estimated discharge of sewage waste based on quantities used...?
	Month Reported
	Quantity of Water Obtained from all sources (litres)
	Quantity of Sewage Waste Discharged
(Estimated)

	January 
	4,319,173.46
	Same

	February 
	4,149,154.30
	Same

	March 
	4,260,276.40
	Same

	April 
	3,843,265.90
	Same

	May 
	3,964,487.90
	Same

	June 
	4,060,054.60
	Same

	July 
	3,932,736.00
	Same

	August 
	3,277,986.90
	Same

	September 
	4,197,288.10
	Same

	October 
	4,369,821.10
	Same

	November
	3,949,206.00
	Same

	December 
	4,094,689.70
	Same

	ANNUAL TOTAL
	48,418,440.36
	


             Note: The water consumption volume is considered equal to the discharge volume 

              because there is no meter at the end of the discharge pipe.
iv. A summary of modifications and/or major maintenance work carried out on the Water Supply and Waste Disposal Facilities, including all associated structures and facilities;



The major modification works were carried out to the new Water Treatment Plant. A water circulation system has been established in the serpentine pipes at the basement of the plant building. Also one micron filter is being bypassed. Currently 20 and 5 micron cartridge filters are successfully being used in the plant.
The old plant is connected with the Generator installed inside the new plant in case of emergency the old plant is required to operate.

The sludge from the WWTP is bagged into the geo tube and dumped in the landfill site. The sludge remains inside the bag as containment. 

          ___________________________________________________________________
v. A list of unauthorized discharges and summary of follow-up action taken;    


The Leachate from the metal dump and the landfill site are uncontrolled. Especially during rainy reason, the surface runoff moves so fast from the right side of the road to the left side of the road through the culverts towards the sea.
Spills:

May 19, 2018: Petroleum Fuel oil: 210 litres;

June 11, 2018: Petroleum fuel oil: Unknown quantity

A drainage plan was proposed already. This plan is being upgraded this summer to submit to NWB along with 2019 Annual Report.

vi. A summary of any abandonment and restoration work completed during the year and an outline of any work anticipated for the next year; 


 No abandonment and restoration work was conducted during this reporting year. 
 However, Hamlet is planning to decommission the old Water Treatment Plant and the old sewage lagoon within a year or two. They prefer using the old truck filling station building for future storage. 

           ________________________________________________________________ 
vii. A summary of any studies requested by the Board that relate to waste disposal, water use or reclamation, and a brief description of any future studies planned;

______________________________________________________________________

Under the current Type A Water Licence # 3AM-PAN1828, the following studies are recommended:
Water supply system:

1. Hydrology study by 2022: This Hydrology study shall address relevant intervener’s comments and recommendations made during 2017-18 licensing process, including, at a minimum, details related to the discharge volume and velocity, erosion, sedimentation, water quality, and variability of discharge into the Duval River.
The Licensee shall withdraw water from the Duval River at a rate that shall not exceed ten percent (10%) of the instantaneous flow in the river, and shall cease all water withdrawal when the instantaneous flow in the river is below thirty percent (30%) of the mean annual discharge.

The licensee shall limit the withdrawal of water from the Duval River to the Months of July and August, unless otherwise recommended by the hydrology study as mentioned above.

Wastes Management: 

· Control surface runoff from the wastes sites

· Erect a fence surrounding the metal wastes and Hazardous wastes Area

· Prepare the standalone drainage /Seepage Monitoring Plan
· Proper storage of the waste oil drums 

           __________________________________________________________________

viii. Any other details on water use or waste disposal requested by the Board by November 1st of the year being reported; and


           Wastes Management: 

· Control surface runoff from the wastes sites

· Erect a fence surrounding the metal wastes and Hazardous wastes Area

· Prepare the standalone drainage /Seepage Monitoring Plan

· Proper storage of the waste oil drums 

· Fish wastes should be treated with lime and covered with soil prior to the onset of the annual spring freshet and then weekly thereafter during June, July, August and September.

Water body:

· No removal any material is recommended from below the ordinary high water mark.
· Can not cause erosion to the banks of the water body.

· Install a flow meter and a fish screen at the Intake pipe

It is noted that a flow meter was already installed. Hamlet is working on the suitable fish screen this summer.
           ________________________________________________________________

ix. Updates or revisions to the approved Operation and Maintenance Plans.

     ________________________________________________________________  

The O&M manual of the Water Treatment Plant has been updated and will be sent within a month to NWB.
           ______________________________________________________________________

     x.       ADDITIONAL INFORMATION THAT THE LICENSEE DEEMS USEFUL:

                     Hamlet has started extended sampling and testing program for toxicity testing using 

                 ALS Lab in Winnipeg. They submitted QA/QC Plan, Spill Contingency Plan and the 
                WWTP bypassing Plan already to the NWB.
                 A consultant is expected to start feasibility study on the Community waste 

                 management from the next financial year. They will also review the previous studies 

                 done for the community wastes site` in order to design a better waste management 

                 process.

    xi.          FOLLOW-UP REGARDING INSPECTION/COMPLIANCE CONCERNS:


               In the new water licence, Hamlet has a permit 120,000 cubic meters water extraction annually 
             from the Duval River. It is only required for the year when the storage reservoir is made empty for 
             cleaning purposes. For regular operation, roughly 60,000 cubic meters water needs to be extracted. 
             The Community’s annual consumption volume is close to 50,000 cubic meters. A good amount of 
             water   is consumed for dust control and in the Fish plant. It is recorded that about 11,000 cubic 
             meters sludge is produced in the WWTP annually and is dumped in the containment geo tube 
            once or  sometimes  twice in a month at the designated area within the land fill site.

             The Test Lab Results for 2018 are submitted in a separate document.
          Hamlet experienced difficulty for shipping samples for Toxicity testing to ALS lab in 

          Winnipeg due to too many transit points of the Cargo. Delivering samples is challenging 

          to  the Lab within a certain time period and samples become spoiled.                                           

                     
[image: image1.emf]
Page 1 of 1

