## B18-15555
Certificate of Analysis | [7 empty] | REPORT No. B18-15555
Final Report
Report To: |  |  |  |  | Caduceon Environmental Laboratories
Hamlet of Pangnirtung |  |  |  |  | 2378 Holly Lane
P.O. Box 253, |  |  |  |  | Ottawa Ontario K1V 7P1
Pangnirtung Nunavut X0A 0R0 Canada |  |  |  |  | Tel: 613-526-0123
Attention: | SAO - |  |  |  | Fax: 613-526-1244
DATE SUBMITTED: | 2018-06-05 10:35 |  |  |  | JOB/PROJECT NO.: |  | Drinking Water
DATE REPORTED: | 2018-06-15 |  |  |  | P.O. NUMBER:
SAMPLE MATRIX: | Drinking Water |  |  |  | WATERWORKS NO.:
|  |  | Client ID: |  | Water Truck Fill Station | Water Truck #604
|  |  | Sample ID: |  | B18-15555-1 | B18-15555-2
|  |  | Date Collected: |  | 30-May-18 | 30-May-18
Parameter | Units | M.D.L. | Reference Method | Date/Site Analyzed
TDS (Calc. from Cond.) | mg/L | 1 | Calc. | 2018-06-08 | 8 | 9
Turbidity | NTU | 0.1 | SM 2130 | 07-Jun-18/O | 0.5 | 0.5
Chloride | mg/L | 0.5 | SM4110C | 05-Jun-18/O | 3.3 | 3.5
Nitrate (N) | mg/L | 0.1 | SM4110C | 05-Jun-18/O | < 0.1 | < 0.1
Nitrite (N) | mg/L | 0.1 | SM4110C | 05-Jun-18/O | < 0.1 | < 0.1
Sulphate | mg/L | 1 | SM4110C | 05-Jun-18/O | 3 | 3
Fluoride | mg/L | 0.1 | SM4110C | 05-Jun-18/O | < 0.1 | < 0.1
Surfactants Content | mg/L | 0.05 | SM-5540-C | 14-Jun-18/O | 0.1 | 0.05
Phenolics | mg/L | 0.001 | MOEE 3179 | 08-Jun-18/O | 0.021 | < 0.001
Dissolved Organic Carbon | mg/L | 0.2 | EPA 415.1 | 08-Jun-18/O | 2 | 1.5
Barium | mg/L | 0.001 | SM 3120 | 06-Jun-18/O | 0.001 | 0.001
Chromium (VI) | mg/L | 0.001 | MOE E3056 | 11-Jun-18/O | < 0.001 | < 0.001
Copper | mg/L | 0.002 | SM 3120 | 06-Jun-18/O | 0.049 | 0.003
Iron | mg/L | 0.005 | SM 3120 | 06-Jun-18/O | 0.012 | 0.009
Manganese | mg/L | 0.001 | SM 3120 | 06-Jun-18/O | 0.016 | 0.016
Zinc | mg/L | 0.005 | SM 3120 | 06-Jun-18/O | 0.087 | 0.011
E coli | cfu/100mL | 1 | MOE E3407 | 05-Jun-18/O | 0 | 0
Cyanide (Total) | mg/L | 0.005 | SM 4500CN | 07-Jun-18/K | < 0.005 | < 0.005
Arsenic | mg/L | 0.0001 | EPA 200.8 | 08-Jun-18/O | < 0.0001 | < 0.0001
Cadmium | mg/L | 1.5e-05 | EPA 200.8 | 08-Jun-18/O | 2.3e-05 | < 0.000015
Lead | mg/L | 2e-05 | EPA 200.8 | 08-Jun-18/O | 0.0143 | 6e-05
Selenium | mg/L | 0.001 | EPA 200.8 | 08-Jun-18/O | < 0.001 | < 0.001
Silver | mg/L | 0.0001 | EPA 200.8 | 08-Jun-18/O | < 0.0001 | < 0.0001

## B18-25991
Certificate of Analysis | [7 empty] | REPORT No. B18-25991
Final Report
Report To: |  |  |  |  | Caduceon Environmental Laboratories
Hamlet of Pangnirtung |  |  |  |  | 2378 Holly Lane
P.O. Box 253, |  |  |  |  | Ottawa Ontario K1V 7P1
Pangnirtung Nunavut X0A 0R0 Canada |  |  |  |  | Tel: 613-526-0123
Attention: | SAO - |  |  |  | Fax: 613-526-1244
DATE SUBMITTED: | 2018-08-29 09:26 |  |  |  | JOB/PROJECT NO.: |  | Drinking Water
DATE REPORTED: | 2018-09-12 |  |  |  | P.O. NUMBER:
SAMPLE MATRIX: | Drinking Water |  |  |  | WATERWORKS NO.:
|  |  | Client ID: |  | Effluent/ WWTP | Duval River
|  |  | Sample ID: |  | B18-25991-1 | B18-25991-2
|  |  | Date Collected: |  | 22-Aug-18 | 22-Aug-18
Parameter | Units | M.D.L. | Reference Method | Date/Site Analyzed
TDS (Calc. from Cond.) | mg/L | 1 | Calc. | 2018-08-31 | 327 | 3
Chloride | mg/L | 0.5 | SM4110C | 29-Aug-18/O | 56.6 | 0.9
Fluoride | mg/L | 0.1 | SM4110C | 29-Aug-18/O | < 0.1 | < 0.1
Nitrate (N) | mg/L | 0.1 | SM4110C | 29-Aug-18/O | 35.9 | < 0.1
Nitrite (N) | mg/L | 0.1 | SM4110C | 29-Aug-18/O | < 0.1 | < 0.1
Sulphate | mg/L | 1 | SM4110C | 29-Aug-18/O | 31 | < 1
Cyanide (Total) | mg/L | 0.005 | SM 4500CN | 30-Aug-18/K | < 0.005 | < 0.005
Arsenic | mg/L | 0.0001 | EPA 200.8 | 29-Aug-18/O | 0.0008 | < 0.0001
Barium | mg/L | 0.001 | SM 3120 | 31-Aug-18/O | < 0.001 | < 0.001
Cadmium | mg/L | 1.5e-05 | EPA 200.8 | 29-Aug-18/O | 0.000131 | < 0.000015
Chromium | mg/L | 0.002 | SM 3120 | 31-Aug-18/O | < 0.002 | < 0.002
Chromium (VI) | mg/L | 0.002 | MOE E3056 | 04-Sep-18/O | < 0.002 | < 0.002
Copper | mg/L | 0.002 | SM 3120 | 31-Aug-18/O | 0.1 | < 0.002
Iron | mg/L | 0.005 | SM 3120 | 31-Aug-18/O | 0.121 | 0.013
Lead | mg/L | 2e-05 | EPA 200.8 | 29-Aug-18/O | 0.00592 | < 0.00002
Manganese | mg/L | 0.001 | SM 3120 | 31-Aug-18/O | 0.035 | 0.001
Selenium | mg/L | 0.001 | EPA 200.8 | 29-Aug-18/O | < 0.001 | < 0.001
Silver | mg/L | 0.0001 | EPA 200.8 | 29-Aug-18/O | < 0.0001 | < 0.0001
Zinc | mg/L | 0.005 | SM 3120 | 31-Aug-18/O | 0.313 | < 0.005
Phenolics | mg/L | 0.002 | MOEE 3179 | 31-Aug-18/K | 0.003 | < 0.002
Dissolved Organic Carbon | mg/L | 0.2 | EPA 415.1 | 30-Aug-18/O | 14.9 | 1.2
Surfactants Content | mg/L | 0.05 | SM-5540-C | 10-Sep-18/O | 0.12 | < 0.05
E coli | cfu/100mL | 1 | MOE E3407 | 29-Aug-18/O | 5 | 3

## B18-21512
Certificate of Analysis | [7 empty] | REPORT No. B18-21512
Final Report
Report To: |  |  |  |  | Caduceon Environmental Laboratories
Hamlet of Pangnirtung |  |  |  |  | 2378 Holly Lane
P.O. Box 253, |  |  |  |  | Ottawa Ontario K1V 7P1
Pangnirtung Nunavut X0A 0R0 Canada |  |  |  |  | Tel: 613-526-0123
Attention: |  |  |  |  | Fax: 613-526-1244
DATE SUBMITTED: | 2018-07-23 10:55 |  |  |  | JOB/PROJECT NO.: |  | Landfill Leachate
DATE REPORTED: | 2018-07-31 |  |  |  | P.O. NUMBER:
SAMPLE MATRIX: | Leachate |  |  |  | WATERWORKS NO.:
|  |  | Client ID: |  | Pan 4 Sludge | Pan 5 Solid Waste | Pan 6 Metal Dump
|  |  | Sample ID: |  | B18-21512-1 | B18-21512-2 | B18-21512-3
|  |  | Date Collected: |  | 17-Jul-18 | 17-Jul-18 | 17-Jul-18
Parameter | Units | M.D.L. | Reference Method | Date/Site Analyzed
Hardness (as CaCO3) | mg/L | 1 | SM 3120 | 24-Jul-18/O | 1870 | 20 | 33
Alkalinity(CaCO3) to pH4.5 | mg/L | 5 | SM 2320B | 24-Jul-18/O | 36 | < 5 | 16
pH @25°C | pH Units |  | SM 4500H | 24-Jul-18/O | 7.22 | 6.59 | 7.4
Conductivity @25°C | µmho/cm | 1 | SM 2510B | 24-Jul-18/O | 19300 | 42 | 66
Total Suspended Solids | mg/L | 3 | SM2540D | 24-Jul-18/K | 24 | 18 | < 3
Chloride | mg/L | 0.5 | SM4110C | 26-Jul-18/O | 7080 | 2.8 | 5.3
Nitrite (N) | mg/L | 0.1 | SM4110C | 26-Jul-18/O | < 5 | < 0.1 | < 0.1
Nitrate (N) | mg/L | 0.1 | SM4110C | 26-Jul-18/O | < 5 | < 0.1 | < 0.1
Sulphate | mg/L | 1 | SM4110C | 26-Jul-18/O | 913 | 1 | 6
Aluminum | mg/L | 0.01 | SM 3120 | 24-Jul-18/O | 0.08 | 0.51 | 0.12
Arsenic | mg/L | 0.0005 | EPA 200.8 | 24-Jul-18/O | 0.0015 | < 0.0005 | < 0.0005
Cadmium | mg/L | 0.005 | SM 3120 | 24-Jul-18/O | < 0.005 | < 0.005 | < 0.005
Calcium | mg/L | 0.02 | SM 3120 | 24-Jul-18/O | 137 | 5.26 | 10.1
Chromium | mg/L | 0.002 | SM 3120 | 24-Jul-18/O | < 0.002 | < 0.002 | < 0.002
Cobalt | mg/L | 0.005 | SM 3120 | 24-Jul-18/O | 0.013 | < 0.005 | < 0.005
Copper | mg/L | 0.002 | SM 3120 | 24-Jul-18/O | < 0.002 | 0.003 | 0.003
Iron | mg/L | 0.005 | SM 3120 | 24-Jul-18/O | 3.71 | 0.788 | 1.26
Lead | mg/L | 0.02 | SM 3120 | 24-Jul-18/O | < 0.02 | < 0.02 | < 0.02
Magnesium | mg/L | 0.02 | SM 3120 | 24-Jul-18/O | 372 | 1.57 | 1.85
Manganese | mg/L | 0.001 | SM 3120 | 24-Jul-18/O | 0.157 | 0.016 | 0.066
Mercury | mg/L | 2e-05 | SM 3112 B | 26-Jul-18/O | 2e-05 | 3e-05 | < 0.00002
Nickel | mg/L | 0.01 | SM 3120 | 24-Jul-18/O | < 0.01 | < 0.01 | < 0.01
Potassium | mg/L | 0.1 | SM 3120 | 24-Jul-18/O | 139 | 0.3 | 0.6
Sodium | mg/L | 0.2 | SM 3120 | 24-Jul-18/O | 3780 | 2.9 | 4.6
Zinc | mg/L | 0.005 | SM 3120 | 24-Jul-18/O | 0.076 | 0.033 | 0.191
Ammonia (N)-Total | mg/L | 0.01 | SM4500-NH3-H | 25-Jul-18/K | 0.7 | 0.03 | 0.13
Phosphorus-Total | mg/L | 0.01 | E3199A.1 | 25-Jul-18/K | 0.05 | 0.06 | 0.04
Phenolics | mg/L | 0.001 | MOEE 3179 | 27-Jul-18/K | < 0.1 | 0.003 | 0.003
BOD | mg/L | 3 | SM 5210B | 23-Jul-18/O | < 3 | < 3 | < 3
Total Organic Carbon | mg/L | 0.2 | EPA 415.1 | 24-Jul-18/O | 0.3 | 7.4 | 7.5
Fecal Coliform | cfu/100mL | 1 | MOE E3371 | 23-Jul-18/O | < 10 | 20 | < 10
Benzene | µg/L | 0.5 | EPA 8260 | 24-Jul-18/O | < 0.5 | < 0.5 | < 0.5
Toluene | µg/L | 0.5 | EPA 8260 | 24-Jul-18/O | < 0.5 | < 0.5 | < 0.5
Ethylbenzene | µg/L | 0.5 | EPA 8260 | 24-Jul-18/O | < 0.5 | < 0.5 | < 0.5
Xylene, m,p- | µg/L | 0.4 | EPA 8260 | 24-Jul-18/O | < 0.4 | < 0.4 | < 0.4
Xylene, o- | µg/L | 0.1 | EPA 8260 | 24-Jul-18/O | < 0.1 | < 0.1 | < 0.1
Xylene, m,p,o- | µg/L | 0.4 | EPA 8260 | 24-Jul-18/O | < 0.4 | < 0.4 | < 0.4
Toluene-d8 (SS) | % |  | EPA 8260 | 24-Jul-18/O | 97 | 97 | 97
PHC F1 (C6-C10) | µg/L | 20 | MOE E3421 | 24-Jul-18/O | 39 | < 20 | < 20
PHC F2 (>C10-C16) | µg/L | 50 | MOE E3421 | 25-Jul-18/K | < 50 | < 50 | < 50
PHC F3 (>C16-C34) | µg/L | 400 | MOE E3421 | 25-Jul-18/K | < 400 | < 400 | < 400
PHC F4 (>C34-C50) | µg/L | 400 | MOE E3421 | 25-Jul-18/K | < 400 | < 400 | < 400
Oil & Grease-Total | mg/L | 1 | SM 5520 | 25-Jul-18/K | 2.8 | 3.2 | 3.2
Acenaphthene | µg/L | 0.05 | EPA 8270 | 25-Jul-18/K | < 0.05 | < 0.05 | < 0.05
Acenaphthylene | µg/L | 0.05 | EPA 8270 | 25-Jul-18/K | < 0.05 | < 0.05 | < 0.05
Anthracene | µg/L | 0.05 | EPA 8270 | 25-Jul-18/K | < 0.05 | < 0.05 | < 0.05
Benzo(a)anthracene | µg/L | 0.05 | EPA 8270 | 25-Jul-18/K | < 0.05 | < 0.05 | < 0.05
Benzo(a)pyrene | µg/L | 0.01 | EPA 8270 | 25-Jul-18/K | < 0.01 | < 0.01 | < 0.01
Benzo(b)fluoranthene | µg/L | 0.05 | EPA 8270 | 25-Jul-18/K | < 0.05 | < 0.05 | < 0.05
Benzo(b+k)fluoranthene | µg/L | 0.1 | EPA 8270 | 25-Jul-18/K | < 0.1 | < 0.1 | < 0.1
Benzo(g,h,i)perylene | µg/L | 0.05 | EPA 8270 | 25-Jul-18/K | < 0.05 | < 0.05 | < 0.05
Benzo(k)fluoranthene | µg/L | 0.05 | EPA 8270 | 25-Jul-18/K | < 0.05 | < 0.05 | < 0.05
Chrysene | µg/L | 0.05 | EPA 8270 | 25-Jul-18/K | < 0.05 | < 0.05 | < 0.05
Dibenzo(a,h)anthracene | µg/L | 0.05 | EPA 8270 | 25-Jul-18/K | < 0.05 | < 0.05 | < 0.05
Fluoranthene | µg/L | 0.05 | EPA 8270 | 25-Jul-18/K | < 0.05 | < 0.05 | < 0.05
Fluorene | µg/L | 0.05 | EPA 8270 | 25-Jul-18/K | < 0.05 | < 0.05 | < 0.05
Indeno(1,2,3,-cd)pyrene | µg/L | 0.05 | EPA 8270 | 25-Jul-18/K | < 0.05 | < 0.05 | < 0.05
Methylnaphthalene,1- | µg/L | 0.05 | EPA 8270 | 25-Jul-18/K | < 0.05 | < 0.05 | < 0.05
Methylnaphthalene,2- | µg/L | 0.05 | EPA 8270 | 25-Jul-18/K | < 0.05 | < 0.05 | < 0.05
Naphthalene | µg/L | 0.05 | EPA 8270 | 25-Jul-18/K | < 0.05 | < 0.05 | < 0.05
Phenanthrene | µg/L | 0.05 | EPA 8270 | 25-Jul-18/K | < 0.05 | < 0.05 | < 0.05
Pyrene | µg/L | 0.05 | EPA 8270 | 25-Jul-18/K | < 0.05 | < 0.05 | < 0.05
Terphenyl-d14 (SS) | % rec. | 10 | EPA 8270 | 25-Jul-18/K | 98 | 104 | 99

## B18-07817
Certificate of Analysis | [7 empty] | REPORT No. B18-07817
Final Report
Report To: |  |  |  |  | Caduceon Environmental Laboratories
Hamlet of Pangnirtung |  |  |  |  | 2378 Holly Lane
P.O. Box 253, |  |  |  |  | Ottawa Ontario K1V 7P1
Pangnirtung Nunavut X0A 0R0 Canada |  |  |  |  | Tel: 613-526-0123
Attention: | Shawn Trepanier |  |  |  | Fax: 613-526-1244
DATE SUBMITTED: | 2018-03-28 10:54 |  |  |  | JOB/PROJECT NO.: |  | Waste Water
DATE REPORTED: | 2018-04-05 |  |  |  | P.O. NUMBER:
SAMPLE MATRIX: | Waste Water |  |  |  | WATERWORKS NO.:
|  |  | Client ID: |  | Influent Pan #2 | Effluent Pan #3
|  |  | Sample ID: |  | B18-07817-1 | B18-07817-2
|  |  | Date Collected: |  | 26-Mar-18 | 26-Mar-18
Parameter | Units | M.D.L. | Reference Method | Date/Site Analyzed
Hardness (as CaCO3) | mg/L | 1 | SM 3120 | 29-Mar-18/O | 91 | 45
Alkalinity(CaCO3) to pH4.5 | mg/L | 5 | SM 2320B | 29-Mar-18/O | 408 | 233
pH @25°C | pH Units |  | SM 4500H | 29-Mar-18/O | 7.74 | 8.26
Conductivity @25°C | µmho/cm | 1 | SM 2510B | 29-Mar-18/O | 1670 | 1230
TDS(ion sum calc.) | mg/L | 1 | Calc. | 29-Mar-18/O | 766 | 640
Total Suspended Solids | mg/L | 3 | SM 2540D | 29-Mar-18/O | 104 | 4
Turbidity | NTU | 0.1 | SM 2130 | 28-Mar-18/O | 183 | 0.8
Chloride | mg/L | 0.5 | SM4110C | 28-Mar-18/O | 180 | 152
Nitrite (N) | mg/L | 0.1 | SM4110C | 28-Mar-18/O | < 0.1 | < 0.1
Nitrate (N) | mg/L | 0.1 | SM4110C | 28-Mar-18/O | 0.2 | 12.9
Sulphate | mg/L | 1 | SM4110C | 28-Mar-18/O | 26 | 34
Calcium | mg/L | 0.02 | SM 3120 | 29-Mar-18/O | 17 | 7.22
Magnesium | mg/L | 0.02 | SM 3120 | 29-Mar-18/O | 11.9 | 6.54
Sodium | mg/L | 0.2 | SM 3120 | 29-Mar-18/O | 124 | 205
Potassium | mg/L | 0.1 | SM 3120 | 29-Mar-18/O | 39.3 | 38.2
Aluminum | mg/L | 0.01 | SM 3120 | 29-Mar-18/O | 0.24 | 0.02
Arsenic | mg/L | 0.0005 | EPA 200.8 | 02-Apr-18/O | 0.0074 | 0.0061
Barium | mg/L | 0.001 | SM 3120 | 29-Mar-18/O | 0.02 | < 0.001
Beryllium | mg/L | 0.002 | SM 3120 | 29-Mar-18/O | < 0.002 | < 0.002
Bismuth | mg/L | 0.02 | SM 3120 | 29-Mar-18/O | < 0.02 | < 0.02
Boron | mg/L | 0.005 | SM 3120 | 29-Mar-18/O | 0.238 | 0.111
Cadmium | mg/L | 0.005 | SM 3120 | 29-Mar-18/O | < 0.005 | < 0.005
Chromium | mg/L | 0.002 | SM 3120 | 29-Mar-18/O | 0.002 | < 0.002
Cobalt | mg/L | 0.005 | SM 3120 | 29-Mar-18/O | < 0.005 | < 0.005
Copper | mg/L | 0.002 | SM 3120 | 29-Mar-18/O | 0.141 | 0.061
Iron | mg/L | 0.005 | SM 3120 | 29-Mar-18/O | 0.648 | 0.063
Lead | mg/L | 0.02 | SM 3120 | 29-Mar-18/O | < 0.02 | < 0.02
Lithium | mg/L | 0.01 | SM 3120 | 29-Mar-18/O | < 0.01 | < 0.01
Manganese | mg/L | 0.001 | SM 3120 | 29-Mar-18/O | 0.047 | 0.006
Mercury | mg/L | 2e-05 | SM 3112 B | 29-Mar-18/O | 9e-05 | < 0.00002
Molybdenum | mg/L | 0.01 | SM 3120 | 29-Mar-18/O | < 0.01 | < 0.01
Nickel | mg/L | 0.01 | SM 3120 | 29-Mar-18/O | < 0.01 | < 0.01
Silicon | mg/L | 0.01 | SM 3120 | 29-Mar-18/O | 2.03 | 2.22
Silver | mg/L | 0.005 | SM 3120 | 29-Mar-18/O | < 0.005 | < 0.005
Zinc | mg/L | 0.005 | SM 3120 | 29-Mar-18/O | 0.209 | 0.062
Ammonia (N)-Total | mg/L | 0.01 | MOEE 3364 | 03-Apr-18/O | 95.2 | 0.08
o-Phosphate (P) | mg/L | 0.01 | MOEE 3366 | 03-Apr-18/O | 15.3 | 14.9
Total Kjeldahl Nitrogen | mg/L | 0.1 | E3199A.1 | 29-Mar-18/K | 141 | 1.6
Phosphorus-Total | mg/L | 0.01 | E3199A.1 | 29-Mar-18/K | 19.5 | 14.9
Phenolics | mg/L | 0.001 | MOEE 3179 | 28-Mar-18/O | 0.217 | < 0.001
BOD | mg/L | 3 | SM 5210B | 29-Mar-18/O | 310 | < 3
COD | mg/L | 5 | SM 5220D | 29-Mar-18/O | 695 | 36
Dissolved Organic Carbon | mg/L | 0.2 | EPA 415.1 | 29-Mar-18/O | 73.8 | 15.7
Total Organic Carbon | mg/L | 0.2 | EPA 415.1 | 29-Mar-18/O | 81 | 18.6
Oil & Grease-Total | mg/L | 1 | SM 5520 | 03-Apr-18/K | 36.2 | < 1.0
Total Coliform | cfu/100mL | 1 | MOE E3371 | 28-Mar-18/O | 3200000 | 10
E coli | cfu/100mL | 1 | MOE E3371 | 28-Mar-18/O | 190000 | < 10
Fecal Coliform | cfu/100mL | 1 | MOE E3371 | 28-Mar-18/O | 240000 | < 10
Fecal Strep. | cfu/100mL | 1 | MOE E3371 | 28-Mar-18/O | 290000 | < 10
Anion Sum | meq/L |  | Calc. | 29-Mar-18/O | 13.8 | 10.6
Cation Sum | meq/L |  | Calc. | 29-Mar-18/O | 14.9 | 10.8
% Difference | % |  | Calc. | 29-Mar-18/O | 4.07 | 1.11
Ion Ratio | AS/CS |  | Calc. | 29-Mar-18/O | 0.922 | 0.978
Sodium Adsorption Ratio | - |  | Calc. | 29-Mar-18/O | 5.64 | 13.3
Conductivity (calc.) | µmho/cm |  | Calc. | 29-Mar-18/O | 1540 | 1100
TDS(calc.)/EC(actual) | - |  | Calc. | 29-Mar-18/O | 0.458 | 0.521
EC(calc.)/EC(actual) | - |  | Calc. | 29-Mar-18/O | 0.919 | 0.899
Langelier Index(25°C) | S.I. |  | Calc. | 29-Mar-18/O | 0.0988 | 0.0141

## B18-10235
Certificate of Analysis | [7 empty] | REPORT No. B18-10235
Final Report
Report To: |  |  |  |  | Caduceon Environmental Laboratories
Hamlet of Pangnirtung |  |  |  |  | 2378 Holly Lane
P.O. Box 253, |  |  |  |  | Ottawa Ontario K1V 7P1
Pangnirtung Nunavut X0A 0R0 Canada |  |  |  |  | Tel: 613-526-0123
Attention: | SAO - |  |  |  | Fax: 613-526-1244
DATE SUBMITTED: | 2018-04-20 10:59 |  |  |  | JOB/PROJECT NO.: |  | Waste Water
DATE REPORTED: | 2018-05-01 |  |  |  | P.O. NUMBER:
SAMPLE MATRIX: | Waste Water |  |  |  | WATERWORKS NO.:
|  |  | Client ID: |  | Influent Pan #2 | Effluent Pan #3
|  |  | Sample ID: |  | B18-10235-1 | B18-10235-2
|  |  | Date Collected: |  | 16-Apr-18 | 16-Apr-18
Parameter | Units | M.D.L. | Reference Method | Date/Site Analyzed
Hardness (as CaCO3) | mg/L | 1 | SM 3120 | 26-Apr-18/O | 49 | 44
Alkalinity(CaCO3) to pH4.5 | mg/L | 5 | SM 2320B | 20-Apr-18/O | 358 | 199
pH @25°C | pH Units |  | SM 4500H | 20-Apr-18/O | 7.65 | 8.01
Conductivity @25°C | µmho/cm | 1 | SM 2510B | 20-Apr-18/O | 1010 | 1060
TDS(ion sum calc.) | mg/L | 1 | Calc. | 26-Apr-18/O | 465 | 597
Total Suspended Solids | mg/L | 3 | SM 2540D | 23-Apr-18/O | 180 | 9
Turbidity | NTU | 0.1 | SM 2130 | 23-Apr-18/O | 115 | 0.8
Chloride | mg/L | 0.5 | SM4110C | 20-Apr-18/O | 42.7 | 108
Nitrite (N) | mg/L | 0.1 | SM4110C | 20-Apr-18/O | < 0.1 | < 0.1
Nitrate (N) | mg/L | 0.1 | SM4110C | 20-Apr-18/O | < 0.1 | 21.5
Sulphate | mg/L | 1 | SM4110C | 20-Apr-18/O | 3 | 30
Aluminum | mg/L | 0.01 | SM 3120 | 26-Apr-18/O | 0.59 | 0.02
Arsenic | mg/L | 0.0005 | EPA 200.8 | 23-Apr-18/O | 0.001 | 0.0039
Barium | mg/L | 0.001 | SM 3120 | 26-Apr-18/O | 0.021 | 0.001
Beryllium | mg/L | 0.002 | SM 3120 | 26-Apr-18/O | < 0.002 | < 0.002
Bismuth | mg/L | 0.02 | SM 3120 | 26-Apr-18/O | 0.02 | < 0.02
Boron | mg/L | 0.005 | SM 3120 | 26-Apr-18/O | 0.189 | 0.187
Cadmium | mg/L | 0.005 | SM 3120 | 26-Apr-18/O | < 0.005 | < 0.005
Calcium | mg/L | 0.02 | SM 3120 | 26-Apr-18/O | 12.4 | 7.47
Chromium | mg/L | 0.002 | SM 3120 | 26-Apr-18/O | 0.003 | < 0.002
Cobalt | mg/L | 0.005 | SM 3120 | 26-Apr-18/O | < 0.005 | < 0.005
Copper | mg/L | 0.002 | SM 3120 | 26-Apr-18/O | 0.224 | 0.061
Iron | mg/L | 0.005 | SM 3120 | 26-Apr-18/O | 0.852 | 0.066
Lead | mg/L | 0.02 | SM 3120 | 26-Apr-18/O | < 0.02 | < 0.02
Lithium | mg/L | 0.01 | SM 3120 | 26-Apr-18/O | < 0.01 | < 0.01
Magnesium | mg/L | 0.02 | SM 3120 | 26-Apr-18/O | 4.47 | 6.05
Mercury | mg/L | 2e-05 | SM 3112 B | 23-Apr-18/O | 0.00033 | < 0.00002
Molybdenum | mg/L | 0.01 | SM 3120 | 26-Apr-18/O | < 0.01 | < 0.01
Manganese | mg/L | 0.001 | SM 3120 | 26-Apr-18/O | 0.043 | 0.011
Nickel | mg/L | 0.01 | SM 3120 | 26-Apr-18/O | < 0.01 | < 0.01
Silicon | mg/L | 0.01 | SM 3120 | 26-Apr-18/O | 2.23 | 2.16
Silver | mg/L | 0.005 | SM 3120 | 26-Apr-18/O | < 0.005 | < 0.005
Sodium | mg/L | 0.2 | SM 3120 | 26-Apr-18/O | 52.6 | 201
Zinc | mg/L | 0.005 | SM 3120 | 26-Apr-18/O | 0.257 | 0.067
Ammonia (N)-Total | mg/L | 0.01 | MOEE 3364 | 24-Apr-18/O | 84.9 | 0.02
Total Kjeldahl Nitrogen | mg/L | 0.1 | E3199A.1 | 23-Apr-18/K | 112 | 1.4
o-Phosphate (P) | mg/L | 0.01 | MOEE 3366 | 24-Apr-18/O | 9.45 | 9.98
Phosphorus-Total | mg/L | 0.01 | E3199A.1 | 23-Apr-18/K | 12.4 | 9.98
Phenolics | mg/L | 0.001 | MOEE 3179 | 24-Apr-18/O | 0.435 | < 0.001
BOD | mg/L | 3 | SM 5210B | 20-Apr-18/O | 321 | < 3
COD | mg/L | 5 | SM 5220D | 24-Apr-18/O | 802 | 37
Dissolved Organic Carbon | mg/L | 0.2 | EPA 415.1 | 23-Apr-18/O | 118 | 15.1
Total Organic Carbon | mg/L | 0.2 | EPA 415.1 | 23-Apr-18/O | 140 | 15.8
Oil & Grease-Total | mg/L | 1 | SM 5520 | 25-Apr-18/K | 90.1 | 3.3
Total Coliform | cfu/100mL | 1 | MOE E3371 | 20-Apr-18/O | 128000000 | 10
E coli | cfu/100mL | 1 | MOE E3371 | 20-Apr-18/O | 2800000 | < 2
Fecal Strep. | cfu/100mL | 1 | MOE E3371 | 20-Apr-18/O | 300000 | < 10
Fecal Coliform | cfu/100mL | 1 | MOE E3371 | 20-Apr-18/O | 5500000 | < 10
Anion Sum | meq/L |  | Calc. | 26-Apr-18/O | 8.42 | 9.18
Cation Sum | meq/L |  | Calc. | 26-Apr-18/O | 9.91 | 10.4
% Difference | % |  | Calc. | 26-Apr-18/O | 8.15 | 6.14
Ion Ratio | AS/CS |  | Calc. | 26-Apr-18/O | 0.849 | 0.884
Sodium Adsorption Ratio | - |  | Calc. | 26-Apr-18/O | 3.26 | 13.3
Conductivity (calc.) | µmho/cm |  | Calc. | 26-Apr-18/O | 981 | 1010
TDS(calc.)/EC(actual) | - |  | Calc. | 26-Apr-18/O | 0.461 | 0.562
EC(calc.)/EC(actual) | - |  | Calc. | 26-Apr-18/O | 0.973 | 0.947
Langelier Index(25°C) | S.I. |  | Calc. | 26-Apr-18/O | -0.165 | -0.291

## B18-13372
Certificate of Analysis | [7 empty] | REPORT No. B18-13372
Final Report
Report To: |  |  |  |  | Caduceon Environmental Laboratories
Hamlet of Pangnirtung |  |  |  |  | 2378 Holly Lane
P.O. Box 253, |  |  |  |  | Ottawa Ontario K1V 7P1
Pangnirtung Nunavut X0A 0R0 Canada |  |  |  |  | Tel: 613-526-0123
Attention: | SAO - |  |  |  | Fax: 613-526-1244
DATE SUBMITTED: | 2018-05-16 15:19 |  |  |  | JOB/PROJECT NO.: |  | Waste Water
DATE REPORTED: | 2018-05-29 |  |  |  | P.O. NUMBER:
SAMPLE MATRIX: | Waste Water |  |  |  | WATERWORKS NO.:
|  |  | Client ID: |  | Influent Pan #2 | Effluent Pan #3
|  |  | Sample ID: |  | B18-13372-1 | B18-13372-2
|  |  | Date Collected: |  | 14-May-18 | 14-May-18
Parameter | Units | M.D.L. | Reference Method | Date/Site Analyzed
Hardness (as CaCO3) | mg/L | 1 | SM 3120 | 22-May-18/O | 45 | 40
Alkalinity(CaCO3) to pH4.5 | mg/L | 5 | SM 2320B | 23-May-18/O | 345 | 35
pH @25°C | pH Units |  | SM 4500H | 23-May-18/O | 7.6 | 7.27
Conductivity @25°C | µmho/cm | 1 | SM 2510B | 23-May-18/O | 969 | 590
TDS(ion sum calc.) | mg/L | 1 | Calc. | 24-May-18/O | 461 | 365
Total Suspended Solids | mg/L | 3 | SM 2540D | 17-May-18/O | 220 | < 3
Turbidity | NTU | 0.1 | SM 2130 | 22-May-18/O | 228 | 0.9
Chloride | mg/L | 0.5 | SM4110C | 18-May-18/O | 46.4 | 58.7
Nitrite (N) | mg/L | 0.1 | SM4110C | 18-May-18/O | 0.1 | < 0.1
Nitrate (N) | mg/L | 0.1 | SM4110C | 18-May-18/O | 0.2 | 26.7
Sulphate | mg/L | 1 | SM4110C | 18-May-18/O | 8 | 32
Aluminum | mg/L | 0.01 | SM 3120 | 22-May-18/O | 0.78 | 0.03
Arsenic | mg/L | 0.0001 | EPA 200.8 | 18-May-18/O | 0.0014 | 0.0011
Barium | mg/L | 0.001 | SM 3120 | 22-May-18/O | 0.022 | 0.011
Beryllium | mg/L | 0.002 | SM 3120 | 22-May-18/O | < 0.002 | < 0.002
Bismuth | mg/L | 0.02 | SM 3120 | 22-May-18/O | < 0.02 | < 0.02
Boron | mg/L | 0.005 | SM 3120 | 22-May-18/O | 0.173 | 0.145
Cadmium | mg/L | 0.005 | SM 3120 | 22-May-18/O | < 0.005 | < 0.005
Calcium | mg/L | 0.02 | SM 3120 | 22-May-18/O | 11.1 | 10.4
Chromium | mg/L | 0.002 | SM 3120 | 22-May-18/O | < 0.002 | < 0.002
Cobalt | mg/L | 0.005 | SM 3120 | 22-May-18/O | < 0.005 | < 0.005
Copper | mg/L | 0.002 | SM 3120 | 22-May-18/O | 0.167 | 0.087
Iron | mg/L | 0.005 | SM 3120 | 22-May-18/O | 1.53 | 0.089
Lead | mg/L | 0.02 | SM 3120 | 22-May-18/O | < 0.02 | < 0.02
Lithium | mg/L | 0.01 | SM 3120 | 22-May-18/O | < 0.01 | < 0.01
Magnesium | mg/L | 0.02 | SM 3120 | 22-May-18/O | 4.08 | 3.48
Mercury | mg/L | 2e-05 | SM 3112 B | 24-May-18/O | 0.00012 | < 0.00002
Molybdenum | mg/L | 0.01 | SM 3120 | 22-May-18/O | < 0.01 | < 0.01
Manganese | mg/L | 0.001 | SM 3120 | 22-May-18/O | 0.06 | 0.024
Nickel | mg/L | 0.01 | SM 3120 | 22-May-18/O | < 0.01 | < 0.01
Silicon | mg/L | 0.01 | SM 3120 | 22-May-18/O | < 0.01 | < 0.01
Silver | mg/L | 0.005 | SM 3120 | 22-May-18/O | < 0.005 | < 0.005
Sodium | mg/L | 0.2 | SM 3120 | 22-May-18/O | 46.7 | 88.3
Zinc | mg/L | 0.005 | SM 3120 | 22-May-18/O | 0.178 | 0.1
Ammonia (N)-Total | mg/L | 0.01 | MOEE 3364 | 23-May-18/O | 85.8 | < 0.01
Total Kjeldahl Nitrogen | mg/L | 0.1 | E3199A.1 | 22-May-18/K | 111 | 1.9
o-Phosphate (P) | mg/L | 0.01 | MOEE 3366 | 23-May-18/O | 9.52 | 11.4
Phosphorus-Total | mg/L | 0.01 | E3199A.1 | 23-May-18/K | 11.2 | 11.4
Phenolics | mg/L | 0.001 | MOEE 3179 | 24-May-18/O | 0.271 | < 0.001
BOD | mg/L | 3 | SM 5210B | 17-May-18/O | 178 | < 3
COD | mg/L | 5 | SM 5220D | 25-May-18/O | 969 | 36
Dissolved Organic Carbon | mg/L | 0.2 | EPA 415.1 | 24-May-18/O | 58.5 | 10.1
Total Organic Carbon | mg/L | 0.2 | EPA 415.1 | 23-May-18/O | 74.7 | 31.4
Oil & Grease-Total | mg/L | 1 | SM 5520 | 22-May-18/K | 41.9 | < 1.0
Total Coliform | cfu/100mL | 1 | MOE E3371 | 16-May-18/O | 56000000 | < 10
E coli | cfu/100mL | 1 | MOE E3371 | 16-May-18/O | 840000 | < 10
Fecal Strep. | cfu/100mL | 1 | MOE E3371 | 16-May-18/O | 85000 | < 10
Fecal Coliform | cfu/100mL | 1 | MOE E3371 | 16-May-18/O | 2200000 | < 10
Anion Sum | meq/L |  | Calc. | 24-May-18/O | 8.49 | 4.95
Cation Sum | meq/L |  | Calc. | 24-May-18/O | 9.61 | 5.47
% Difference | % |  | Calc. | 24-May-18/O | 6.17 | 5
Ion Ratio | AS/CS |  | Calc. | 24-May-18/O | 0.884 | 0.905
Sodium Adsorption Ratio | - |  | Calc. | 24-May-18/O | 3.05 | 6.05
Conductivity (calc.) | µmho/cm |  | Calc. | 24-May-18/O | 970 | 596
TDS(calc.)/EC(actual) | - |  | Calc. | 24-May-18/O | 0.476 | 0.618
EC(calc.)/EC(actual) | - |  | Calc. | 24-May-18/O | 1 | 1.01
Langelier Index(25°C) | S.I. |  | Calc. | 24-May-18/O | -0.279 | -1.62

## B18-16046
Certificate of Analysis | [7 empty] | REPORT No. B18-16046
Final Report
Report To: |  |  |  |  | Caduceon Environmental Laboratories
Hamlet of Pangnirtung |  |  |  |  | 2378 Holly Lane
P.O. Box 253, |  |  |  |  | Ottawa Ontario K1V 7P1
Pangnirtung Nunavut X0A 0R0 Canada |  |  |  |  | Tel: 613-526-0123
Attention: | SAO - |  |  |  | Fax: 613-526-1244
DATE SUBMITTED: | 2018-06-07 10:51 |  |  |  | JOB/PROJECT NO.: |  | Waste Water
DATE REPORTED: | 2018-06-15 |  |  |  | P.O. NUMBER:
SAMPLE MATRIX: | Waste Water |  |  |  | WATERWORKS NO.:
|  |  | Client ID: |  | Pam 2 Influent | Pam 3 Effluent
|  |  | Sample ID: |  | B18-16046-1 | B18-16046-2
|  |  | Date Collected: |  | 05-Jun-18 | 05-Jun-18
Parameter | Units | M.D.L. | Reference Method | Date/Site Analyzed
Hardness (as CaCO3) | mg/L | 1 | SM 3120 | 14-Jun-18/O | 73 | 85
Alkalinity(CaCO3) to pH4.5 | mg/L | 5 | SM 2320B | 08-Jun-18/O | 437 | < 5
pH @25°C | pH Units |  | SM 4500H | 08-Jun-18/O | 7.86 | 3.87
Conductivity @25°C | µmho/cm | 1 | SM 2510B | 08-Jun-18/O | 1140 | 785
TDS(ion sum calc.) | mg/L | 1 | Calc. | 14-Jun-18/O | 589 | 433
Total Suspended Solids | mg/L | 3 | SM 2540D | 08-Jun-18/O | 390 | < 3
Turbidity | NTU | 0.1 | SM 2130 | 07-Jun-18/O | 367 | 0.8
Chloride | mg/L | 0.5 | SM4110C | 07-Jun-18/O | 57 | 62.2
Nitrite (N) | mg/L | 0.1 | SM4110C | 07-Jun-18/O | < 0.1 | < 0.1
Nitrate (N) | mg/L | 0.1 | SM4110C | 07-Jun-18/O | < 0.1 | 44.2
Sulphate | mg/L | 1 | SM4110C | 07-Jun-18/O | 21 | 34
Aluminum | mg/L | 0.01 | SM 3120 | 14-Jun-18/O | 2.05 | 0.67
Arsenic | mg/L | 0.0005 | EPA 200.8 | 07-Jun-18/O | < 0.0005 | 0.0011
Barium | mg/L | 0.001 | SM 3120 | 14-Jun-18/O | 0.037 | 0.022
Beryllium | mg/L | 0.002 | SM 3120 | 14-Jun-18/O | < 0.002 | < 0.002
Bismuth | mg/L | 0.02 | SM 3120 | 14-Jun-18/O | < 0.02 | < 0.02
Boron | mg/L | 0.005 | SM 3120 | 14-Jun-18/O | 0.175 | 0.233
Cadmium | mg/L | 0.005 | SM 3120 | 14-Jun-18/O | < 0.005 | < 0.005
Calcium | mg/L | 0.02 | SM 3120 | 14-Jun-18/O | 20.1 | 20
Chromium | mg/L | 0.002 | SM 3120 | 14-Jun-18/O | 0.005 | < 0.002
Cobalt | mg/L | 0.005 | SM 3120 | 14-Jun-18/O | < 0.005 | 0.01
Copper | mg/L | 0.002 | SM 3120 | 14-Jun-18/O | 0.316 | 0.223
Iron | mg/L | 0.005 | SM 3120 | 14-Jun-18/O | 2.56 | 0.214
Lead | mg/L | 0.02 | SM 3120 | 14-Jun-18/O | < 0.02 | < 0.02
Lithium | mg/L | 0.01 | SM 3120 | 14-Jun-18/O | < 0.01 | < 0.01
Magnesium | mg/L | 0.02 | SM 3120 | 14-Jun-18/O | 5.52 | 8.49
Mercury | mg/L | 2e-05 | SM 3112 B | 14-Jun-18/O | 0.00019 | < 0.00002
Molybdenum | mg/L | 0.01 | SM 3120 | 14-Jun-18/O | < 0.01 | < 0.01
Manganese | mg/L | 0.001 | SM 3120 | 14-Jun-18/O | 0.081 | 0.182
Nickel | mg/L | 0.01 | SM 3120 | 14-Jun-18/O | 0.01 | < 0.01
Silicon | mg/L | 0.01 | SM 3120 | 14-Jun-18/O | 3.21 | 2.75
Silver | mg/L | 0.005 | SM 3120 | 14-Jun-18/O | < 0.005 | < 0.005
Sodium | mg/L | 0.2 | SM 3120 | 14-Jun-18/O | 53 | 75.4
Zinc | mg/L | 0.005 | SM 3120 | 14-Jun-18/O | 0.481 | 1.33
Ammonia (N)-Total | mg/L | 0.01 | MOEE 3364 | 13-Jun-18/O | 106 | 0.03
Total Kjeldahl Nitrogen | mg/L | 0.1 | E3199A.1 | 11-Jun-18/K | 147 | 2.5
o-Phosphate (P) | mg/L | 0.01 | MOEE 3366 | 13-Jun-18/O | 11.8 | 22.9
Phosphorus-Total | mg/L | 0.01 | E3199A.1 | 12-Jun-18/K | 16.6 | 27.3
Phenolics | mg/L | 0.001 | MOEE 3179 | 08-Jun-18/O | 0.319 | < 0.001
BOD | mg/L | 3 | SM 5210B | 08-Jun-18/O | 353 | < 3
COD | mg/L | 5 | SM 5220D | 11-Jun-18/O | 1540 | 44
Dissolved Organic Carbon | mg/L | 0.2 | EPA 415.1 | 11-Jun-18/O | 99.2 | 16.4
Total Organic Carbon | mg/L | 0.2 | EPA 415.1 | 11-Jun-18/O | 105 | 17.2
Oil & Grease-Total | mg/L | 1 | SM 5520 | 12-Jun-18/K | 217 | 2.3
Total Coliform | cfu/100mL | 1 | MOE E3371 | 07-Jun-18/O | 75000000 | < 10
E coli | cfu/100mL | 1 | MOE E3371 | 07-Jun-18/O | 3000000 | < 10
Fecal Strep. | cfu/100mL | 1 | MOE E3371 | 07-Jun-18/O | 9500000 | < 10
Fecal Coliform | cfu/100mL | 1 | MOE E3371 | 07-Jun-18/O | 7100000 | < 10
Anion Sum | meq/L |  | Calc. | 14-Jun-18/O | 10.8 | 5.61
Cation Sum | meq/L |  | Calc. | 14-Jun-18/O | 12.1 | 5.95
% Difference | % |  | Calc. | 14-Jun-18/O | 5.54 | 2.91
Ion Ratio | AS/CS |  | Calc. | 14-Jun-18/O | 0.895 | 0.943
Sodium Adsorption Ratio | - |  | Calc. | 14-Jun-18/O | 2.7 | 3.56
Conductivity (calc.) | µmho/cm |  | Calc. | 14-Jun-18/O | 1210 | 680
TDS(calc.)/EC(actual) | - |  | Calc. | 14-Jun-18/O | 0.518 | 0.552
EC(calc.)/EC(actual) | - |  | Calc. | 14-Jun-18/O | 1.07 | 0.866
Langelier Index(25°C) | S.I. |  | Calc. | 14-Jun-18/O | 0.331 | -

## B18-20632
Certificate of Analysis | [7 empty] | REPORT No. B18-20632
Final Report
Report To: |  |  |  |  | Caduceon Environmental Laboratories
Hamlet of Pangnirtung |  |  |  |  | 2378 Holly Lane
P.O. Box 253, |  |  |  |  | Ottawa Ontario K1V 7P1
Pangnirtung Nunavut X0A 0R0 Canada |  |  |  |  | Tel: 613-526-0123
Attention: | SAO - |  |  |  | Fax: 613-526-1244
DATE SUBMITTED: | 2018-07-16 12:04 |  |  |  | JOB/PROJECT NO.: |  | Waste Water
DATE REPORTED: | 2018-07-24 |  |  |  | P.O. NUMBER:
SAMPLE MATRIX: | Waste Water |  |  |  | WATERWORKS NO.:
|  |  | Client ID: |  | Pam 2 Influent | Pam 3 Effluent
|  |  | Sample ID: |  | B18-20632-1 | B18-20632-2
|  |  | Date Collected: |  | 10-Jul-18 | 10-Jul-18
Parameter | Units | M.D.L. | Reference Method | Date/Site Analyzed
Hardness (as CaCO3) | mg/L | 1 | SM 3120 | 17-Jul-18/O | 56 | 27
Alkalinity(CaCO3) to pH4.5 | mg/L | 5 | SM 2320B | 17-Jul-18/O | 336 | 52
pH @25°C | pH Units |  | SM 4500H | 17-Jul-18/O | 7.48 | 7.38
Conductivity @25°C | µmho/cm | 1 | SM 2510B | 17-Jul-18/O | 1100 | 579
TDS(ion sum calc.) | mg/L | 1 | Calc. | 18-Jul-18/O | 474 | 335
Total Suspended Solids | mg/L | 3 | SM 2540D | 17-Jul-18/O | 320 | < 3
Turbidity | NTU | 0.1 | SM 2130 | 16-Jul-18/O | 238 | 0.5
Chloride | mg/L | 0.5 | SM4110C | 18-Jul-18/O | 52.9 | 57.3
Nitrite (N) | mg/L | 0.1 | SM4110C | 18-Jul-18/O | < 0.1 | < 0.1
Nitrate (N) | mg/L | 0.1 | SM4110C | 18-Jul-18/O | < 0.1 | 19.1
Sulphate | mg/L | 1 | SM4110C | 18-Jul-18/O | 5 | 35
Aluminum | mg/L | 0.01 | SM 3120 | 17-Jul-18/O | 0.86 | 0.02
Arsenic | mg/L | 0.0005 | EPA 200.8 | 23-Jul-18/O | 0.0007 | < 0.0005
Barium | mg/L | 0.001 | SM 3120 | 17-Jul-18/O | 0.027 | 0.001
Beryllium | mg/L | 0.002 | SM 3120 | 17-Jul-18/O | < 0.002 | < 0.002
Bismuth | mg/L | 0.02 | SM 3120 | 17-Jul-18/O | < 0.02 | < 0.02
Boron | mg/L | 0.005 | SM 3120 | 17-Jul-18/O | 0.214 | 0.215
Cadmium | mg/L | 0.005 | SM 3120 | 17-Jul-18/O | < 0.005 | < 0.005
Calcium | mg/L | 0.02 | SM 3120 | 17-Jul-18/O | 14.8 | 6.25
Chromium | mg/L | 0.002 | SM 3120 | 17-Jul-18/O | 0.003 | < 0.002
Cobalt | mg/L | 0.005 | SM 3120 | 17-Jul-18/O | < 0.005 | < 0.005
Copper | mg/L | 0.002 | SM 3120 | 17-Jul-18/O | 0.2 | 0.104
Iron | mg/L | 0.005 | SM 3120 | 17-Jul-18/O | 1.81 | 0.078
Lead | mg/L | 0.02 | SM 3120 | 17-Jul-18/O | < 0.02 | < 0.02
Lithium | mg/L | 0.01 | SM 3120 | 17-Jul-18/O | < 0.01 | < 0.01
Magnesium | mg/L | 0.02 | SM 3120 | 17-Jul-18/O | 4.51 | 2.65
Manganese | mg/L | 0.001 | SM 3120 | 17-Jul-18/O | 0.059 | 0.007
Mercury | mg/L | 2e-05 | SM 3112 B | 18-Jul-18/O | 9e-05 | < 0.00002
Molybdenum | mg/L | 0.01 | SM 3120 | 17-Jul-18/O | < 0.01 | 0.01
Nickel | mg/L | 0.01 | SM 3120 | 17-Jul-18/O | 0.01 | < 0.01
Silicon | mg/L | 0.01 | SM 3120 | 17-Jul-18/O | 1.79 | 2
Silver | mg/L | 0.005 | SM 3120 | 17-Jul-18/O | < 0.005 | < 0.005
Sodium | mg/L | 0.2 | SM 3120 | 17-Jul-18/O | 47.7 | 90.7
Zinc | mg/L | 0.005 | SM 3120 | 17-Jul-18/O | 0.307 | 0.114
Ammonia (N)-Total | mg/L | 0.01 | MOEE 3364 | 18-Jul-18/O | 89.7 | < 0.01
Total Kjeldahl Nitrogen | mg/L | 0.1 | E3199A.1 | 18-Jul-18/K | 119 | 1.7
o-Phosphate (P) | mg/L | 0.01 | MOEE 3366 | 18-Jul-18/O | 10.5 | 11.6
Phosphorus-Total | mg/L | 0.01 | E3199A.1 | 18-Jul-18/K | 13.1 | 12.5
Phenolics | mg/L | 0.001 | MOEE 3179 | 19-Jul-18/K | 0.439 | 0.003
BOD | mg/L | 3 | SM 5210B | 16-Jul-18/O | 331 | < 3
COD | mg/L | 5 | SM 5220D | 17-Jul-18/O | 800 | 35
Dissolved Organic Carbon | mg/L | 0.2 | EPA 415.1 | 17-Jul-18/O | 122 | 11.8
Total Organic Carbon | mg/L | 0.2 | EPA 415.1 | 17-Jul-18/O | 138 | 12.7
Oil & Grease-Total | mg/L | 1 | SM 5520 | 19-Jul-18/K | 61.2 | 2.7
Total Coliform | cfu/100mL | 1 | MOE E3371 | 16-Jul-18/O | 79000000 | < 10
E coli | cfu/100mL | 1 | MOE E3371 | 16-Jul-18/O | 920000 | < 10
Fecal Strep. | cfu/100mL | 1 | MOE E3371 | 16-Jul-18/O | 36000 | < 10
Fecal Coliform | cfu/100mL | 1 | MOE E3371 | 16-Jul-18/O | 840000 | < 10
Anion Sum | meq/L |  | Calc. | 18-Jul-18/O | 8.59 | 4.75
Cation Sum | meq/L |  | Calc. | 18-Jul-18/O | 10.2 | 5.17
% Difference | % |  | Calc. | 18-Jul-18/O | 8.64 | 4.26
Ion Ratio | AS/CS |  | Calc. | 18-Jul-18/O | 0.841 | 0.918
Sodium Adsorption Ratio | - |  | Calc. | 18-Jul-18/O | 2.79 | 7.66
Conductivity (calc.) | µmho/cm |  | Calc. | 18-Jul-18/O | 1000 | 559
TDS(calc.)/EC(actual) | - |  | Calc. | 18-Jul-18/O | 0.431 | 0.578
EC(calc.)/EC(actual) | - |  | Calc. | 18-Jul-18/O | 0.912 | 0.966
Langelier Index(25°C) | S.I. |  | Calc. | 18-Jul-18/O | -0.286 | -1.66

## B18-24264
Certificate of Analysis | [7 empty] | REPORT No. B18-24264
Final Report
Report To: |  |  |  |  | Caduceon Environmental Laboratories
Hamlet of Pangnirtung |  |  |  |  | 2378 Holly Lane
P.O. Box 253, |  |  |  |  | Ottawa Ontario K1V 7P1
Pangnirtung Nunavut X0A 0R0 Canada |  |  |  |  | Tel: 613-526-0123
Attention: | SAO - |  |  |  | Fax: 613-526-1244
DATE SUBMITTED: | 2018-08-15 10:27 |  |  |  | JOB/PROJECT NO.: |  | Waste Water
DATE REPORTED: | 2018-08-22 |  |  |  | P.O. NUMBER:
SAMPLE MATRIX: | Waste Water |  |  |  | WATERWORKS NO.:
|  |  | Client ID: |  | Influent Pan 2 | Influent Pan 3
|  |  | Sample ID: |  | B18-24264-1 | B18-24264-2
|  |  | Date Collected: |  | 13-Aug-18 | 13-Aug-18
Parameter | Units | M.D.L. | Reference Method | Date/Site Analyzed
Hardness (as CaCO3) | mg/L | 1 | SM 3120 | 21-Aug-18/O | 52 | 86
Alkalinity(CaCO3) to pH4.5 | mg/L | 5 | SM 2320B | 15-Aug-18/O | 356 | < 5
pH @25°C | pH Units |  | SM 4500H | 15-Aug-18/O | 7.61 | 5.8
Conductivity @25°C | µmho/cm | 1 | SM 2510B | 15-Aug-18/O | 1100 | 586
TDS(ion sum calc.) | mg/L | 1 | Calc. | 21-Aug-18/O | 506 | 364
Total Suspended Solids | mg/L | 3 | SM 2540D | 16-Aug-18/O | 510 | 86
Turbidity | NTU | 0.1 | SM 2130 | 15-Aug-18/O | 199 | 18.8
Chloride | mg/L | 0.5 | SM4110C | 15-Aug-18/O | 56.1 | 55
Nitrite (N) | mg/L | 0.1 | SM4110C | 15-Aug-18/O | < 0.1 | 0.1
Nitrate (N) | mg/L | 0.1 | SM4110C | 15-Aug-18/O | < 0.1 | 28.8
Sulphate | mg/L | 1 | SM4110C | 15-Aug-18/O | 9 | 35
Aluminum | mg/L | 0.01 | SM 3120 | 21-Aug-18/O | 1.55 | 1.04
Arsenic | mg/L | 0.0001 | EPA 200.8 | 16-Aug-18/O | 0.0014 | 0.0015
Barium | mg/L | 0.001 | SM 3120 | 21-Aug-18/O | 0.031 | 0.036
Beryllium | mg/L | 0.002 | SM 3120 | 21-Aug-18/O | < 0.002 | < 0.002
Bismuth | mg/L | 0.02 | SM 3120 | 21-Aug-18/O | < 0.02 | 0.03
Boron | mg/L | 0.005 | SM 3120 | 21-Aug-18/O | 0.32 | 0.292
Cadmium | mg/L | 0.005 | SM 3120 | 21-Aug-18/O | < 0.005 | < 0.005
Calcium | mg/L | 0.02 | SM 3120 | 21-Aug-18/O | 13.6 | 22.6
Chromium | mg/L | 0.002 | SM 3120 | 21-Aug-18/O | 0.006 | 0.007
Cobalt | mg/L | 0.005 | SM 3120 | 21-Aug-18/O | < 0.005 | < 0.005
Copper | mg/L | 0.002 | SM 3120 | 21-Aug-18/O | 0.239 | 0.409
Iron | mg/L | 0.005 | SM 3120 | 21-Aug-18/O | 2.06 | 1.64
Lead | mg/L | 0.02 | SM 3120 | 21-Aug-18/O | < 0.02 | 0.11
Lithium | mg/L | 0.01 | SM 3120 | 21-Aug-18/O | < 0.01 | < 0.01
Magnesium | mg/L | 0.02 | SM 3120 | 21-Aug-18/O | 4.43 | 7.08
Manganese | mg/L | 0.001 | SM 3120 | 21-Aug-18/O | 0.062 | 0.148
Mercury | mg/L | 2e-05 | SM 3112 B | 21-Aug-18/O | 0.00016 | 0.00162
Molybdenum | mg/L | 0.01 | SM 3120 | 21-Aug-18/O | < 0.01 | < 0.01
Nickel | mg/L | 0.01 | SM 3120 | 21-Aug-18/O | < 0.01 | 0.01
Potassium | mg/L | 0.1 | SM 3120 | 21-Aug-18/O | 28.7 | 36
Silicon | mg/L | 0.01 | SM 3120 | 21-Aug-18/O | 2.14 | 3.66
Silver | mg/L | 0.005 | SM 3120 | 21-Aug-18/O | < 0.005 | < 0.005
Sodium | mg/L | 0.2 | SM 3120 | 21-Aug-18/O | 50.8 | 76.5
Zinc | mg/L | 0.005 | SM 3120 | 21-Aug-18/O | 0.39 | 0.978
Ammonia (N)-Total | mg/L | 0.01 | MOEE 3364 | 15-Aug-18/O | 99.1 | 0.06
Total Kjeldahl Nitrogen | mg/L | 0.1 | E3199A.1 | 17-Aug-18/K | 138 | 6
o-Phosphate (P) | mg/L | 0.01 | MOEE 3366 | 15-Aug-18/O | 11.2 | 16.7
Phosphorus-Total | mg/L | 0.01 | E3199A.1 | 17-Aug-18/K | 16.2 | 15.8
Phenolics | mg/L | 0.002 | MOEE 3179 | 17-Aug-18/K | 0.28 | 0.003
BOD | mg/L | 3 | SM 5210B | 16-Aug-18/O | 411 | 58
COD | mg/L | 5 | SM 5220D | 17-Aug-18/O | 1360 | 128
Dissolved Organic Carbon | mg/L | 0.2 | EPA 415.1 | 17-Aug-18/O | 83.5 | 10.7
Total Organic Carbon | mg/L | 0.2 | EPA 415.1 | 17-Aug-18/O | 86.5 | 11.1
Oil & Grease-Total | mg/L | 1 | SM 5520 | 20-Aug-18/K | 82.4 | < 1.0
Total Coliform | cfu/100mL | 1 | MOE E3371 | 15-Aug-18/O | 50000000 | 74000
E coli | cfu/100mL | 1 | MOE E3371 | 15-Aug-18/O | 770000 | 1700
Fecal Strep. | cfu/100mL | 1 | MOE E3371 | 15-Aug-18/O | 700000 | 1400
Fecal Coliform | cfu/100mL | 1 | MOE E3371 | 15-Aug-18/O | 2200000 | 3900
Anion Sum | meq/L |  | Calc. | 21-Aug-18/O | 8.88 | 4.44
Cation Sum | meq/L |  | Calc. | 21-Aug-18/O | 11 | 6.06
% Difference | % |  | Calc. | 21-Aug-18/O | 10.9 | 15.4
Ion Ratio | AS/CS |  | Calc. | 21-Aug-18/O | 0.804 | 0.733
Sodium Adsorption Ratio | - |  | Calc. | 21-Aug-18/O | 3.06 | 3.6
Conductivity (calc.) | µmho/cm |  | Calc. | 21-Aug-18/O | 1080 | 599
TDS(calc.)/EC(actual) | - |  | Calc. | 21-Aug-18/O | 0.46 | 0.621
EC(calc.)/EC(actual) | - |  | Calc. | 21-Aug-18/O | 0.985 | 1.02
Langelier Index(25°C) | S.I. |  | Calc. | 21-Aug-18/O | -0.168 | -3.75

## B18-28781
Certificate of Analysis | [7 empty] | REPORT No. B18-28781
Final Report
Report To: |  |  |  |  | Caduceon Environmental Laboratories
Hamlet of Pangnirtung |  |  |  |  | 2378 Holly Lane
P.O. Box 253, |  |  |  |  | Ottawa Ontario K1V 7P1
Pangnirtung Nunavut X0A 0R0 Canada |  |  |  |  | Tel: 613-526-0123
Attention: | SAO - |  |  |  | Fax: 613-526-1244
DATE SUBMITTED: | 2018-09-20 13:26 |  |  |  | JOB/PROJECT NO.: |  | Waste Water
DATE REPORTED: | 2018-10-05 |  |  |  | P.O. NUMBER:
SAMPLE MATRIX: | Waste Water |  |  |  | WATERWORKS NO.:
|  |  | Client ID: |  | Pan 2 Influent | Pam 3 Effluent
|  |  | Sample ID: |  | B18-28781-1 | B18-28781-2
|  |  | Date Collected: |  | 18-Sep-18 | 18-Sep-18
Parameter | Units | M.D.L. | Reference Method | Date/Site Analyzed
Hardness (as CaCO3) | mg/L | 1 | SM 3120 | 27-Sep-18/O | 78 | 37
Alkalinity(CaCO3) to pH4.5 | mg/L | 5 | SM 2320B | 24-Sep-18/O | 378 | 17
pH @25°C | pH Units |  | SM 4500H | 24-Sep-18/O | 7.73 | 6.67
Conductivity @25°C | µmho/cm | 1 | SM 2510B | 24-Sep-18/O | 1070 | 700
TDS(ion sum calc.) | mg/L | 1 | Calc. | 28-Sep-18/O | 525 | 433
Total Suspended Solids | mg/L | 3 | SM 2540D | 24-Sep-18/O | 420 | < 3
Turbidity | NTU | 0.1 | SM 2130 | 21-Sep-18/O | 296 | 0.3
Chloride | mg/L | 0.5 | SM4110C | 25-Sep-18/O | 52 | 55.1
Nitrite (N) | mg/L | 0.1 | SM4110C | 25-Sep-18/O | < 0.1 | < 0.1
Nitrate (N) | mg/L | 0.1 | SM4110C | 25-Sep-18/O | < 0.1 | 41.7
Sulphate | mg/L | 1 | SM4110C | 25-Sep-18/O | 11 | 36
Aluminum | mg/L | 0.01 | SM 3120 | 27-Sep-18/O | 2.64 | 0.08
Arsenic | mg/L | 0.0005 | EPA 200.8 | 27-Sep-18/O | 0.0014 | 0.0005
Barium | mg/L | 0.001 | SM 3120 | 27-Sep-18/O | 0.048 | 0.011
Beryllium | mg/L | 0.002 | SM 3120 | 27-Sep-18/O | < 0.002 | < 0.002
Bismuth | mg/L | 0.02 | SM 3120 | 27-Sep-18/O | < 0.02 | < 0.02
Boron | mg/L | 0.005 | SM 3120 | 27-Sep-18/O | 0.162 | 0.168
Cadmium | mg/L | 0.005 | SM 3120 | 27-Sep-18/O | < 0.005 | < 0.005
Calcium | mg/L | 0.02 | SM 3120 | 27-Sep-18/O | 22.3 | 8.91
Chromium | mg/L | 0.002 | SM 3120 | 27-Sep-18/O | 0.009 | < 0.002
Cobalt | mg/L | 0.005 | SM 3120 | 27-Sep-18/O | < 0.005 | < 0.005
Copper | mg/L | 0.002 | SM 3120 | 27-Sep-18/O | 0.346 | 0.075
Iron | mg/L | 0.005 | SM 3120 | 27-Sep-18/O | 3.12 | 0.203
Lead | mg/L | 0.02 | SM 3120 | 27-Sep-18/O | 0.02 | < 0.02
Lithium | mg/L | 0.01 | SM 3120 | 27-Sep-18/O | < 0.01 | < 0.01
Magnesium | mg/L | 0.02 | SM 3120 | 27-Sep-18/O | 5.39 | 3.56
Manganese | mg/L | 0.001 | SM 3120 | 27-Sep-18/O | 0.074 | 0.021
Mercury | mg/L | 2e-05 | SM 3112 B | 27-Sep-18/O | 0.0002 | < 0.00002
Molybdenum | mg/L | 0.01 | SM 3120 | 27-Sep-18/O | < 0.01 | < 0.01
Nickel | mg/L | 0.01 | SM 3120 | 27-Sep-18/O | 0.01 | < 0.01
Silicon | mg/L | 0.01 | SM 3120 | 27-Sep-18/O | 2.64 | 1.84
Silver | mg/L | 0.005 | SM 3120 | 27-Sep-18/O | < 0.005 | < 0.005
Sodium | mg/L | 0.2 | SM 3120 | 27-Sep-18/O | 60.4 | 109
Zinc | mg/L | 0.005 | SM 3120 | 27-Sep-18/O | 0.536 | 0.098
Ammonia (N)-Total | mg/L | 0.01 | SM4500-NH3-H | 24-Sep-18/K | 91.2 | 0.05
Total Kjeldahl Nitrogen | mg/L | 0.1 | E3199A.1 | 21-Sep-18/K | 129 | 2
o-Phosphate (P) | mg/L | 0.01 | PE4500-S | 24-Sep-18/K | 8.93 | 11.3
Phosphorus-Total | mg/L | 0.01 | E3199A.1 | 24-Sep-18/K | 15.7 | 7.9
Phenolics | mg/L | 0.002 | MOEE 3179 | 24-Sep-18/K | 0.258 | 0.003
BOD | mg/L | 3 | SM 5210B | 21-Sep-18/O | 329 | < 3
COD | mg/L | 5 | SM 5220D | 25-Sep-18/O | 1110 | 48
Dissolved Organic Carbon | mg/L | 0.2 | EPA 415.1 | 25-Sep-18/O | 83.9 | 18.1
Total Organic Carbon | mg/L | 0.2 | EPA 415.1 | 25-Sep-18/O | 89.3 | 22.8
Oil & Grease-Total | mg/L | 1 | SM 5520 | 26-Sep-18/K | 61.4 | < 1.0
Total Coliform | cfu/100mL | 1 | MOE E3371 | 20-Sep-18/O | 68000000 | 40
E coli | cfu/100mL | 1 | MOE E3371 | 20-Sep-18/O | 4200000 | < 2
Fecal Strep. | cfu/100mL |  | MOE E3371 | 20-Sep-18/O | NA | NA
Fecal Coliform | cfu/100mL | 1 | MOE E3371 | 20-Sep-18/O | 4500000 | 24
Anion Sum | meq/L |  | Calc. | 28-Sep-18/O | 9.34 | 5.63
Cation Sum | meq/L |  | Calc. | 28-Sep-18/O | 11.4 | 6.15
% Difference | % |  | Calc. | 28-Sep-18/O | 9.81 | 4.43
Ion Ratio | AS/CS |  | Calc. | 28-Sep-18/O | 0.821 | 0.915
Sodium Adsorption Ratio | - |  | Calc. | 28-Sep-18/O | 2.98 | 7.81
Conductivity (calc.) | µmho/cm |  | Calc. | 28-Sep-18/O | 1090 | 676
TDS(calc.)/EC(actual) | - |  | Calc. | 28-Sep-18/O | 0.493 | 0.619
EC(calc.)/EC(actual) | - |  | Calc. | 28-Sep-18/O | 1.02 | 0.966
Langelier Index(25°C) | S.I. |  | Calc. | 28-Sep-18/O | 0.193 | -2.61

## B18-34080
Certificate of Analysis | [7 empty] | REPORT No. B18-34080
Final Report
Report To: |  |  |  |  | Caduceon Environmental Laboratories
Hamlet of Pangnirtung |  |  |  |  | 2378 Holly Lane
P.O. Box 253, |  |  |  |  | Ottawa Ontario K1V 7P1
Pangnirtung Nunavut X0A 0R0 Canada |  |  |  |  | Tel: 613-526-0123
Attention: | SAO - |  |  |  | Fax: 613-526-1244
DATE SUBMITTED: | 2018-11-05 11:01 |  |  |  | JOB/PROJECT NO.: |  | Waste Water
DATE REPORTED: | 2018-11-16 |  |  |  | P.O. NUMBER:
SAMPLE MATRIX: | Waste Water |  |  |  | WATERWORKS NO.:
|  |  | Client ID: |  | Pan 2 Influent | Pan 3 Effluent
|  |  | Sample ID: |  | B18-34080-1 | B18-34080-2
|  |  | Date Collected: |  | 23-Oct-18 | 23-Oct-18
Parameter | Units | M.D.L. | Reference Method | Date/Site Analyzed
Hardness (as CaCO3) | mg/L | 1 | SM 3120 | 13-Nov-18/O | 57 | 53
Alkalinity(CaCO3) to pH4.5 | mg/L | 5 | SM 2320B | 07-Nov-18/O | 405 | 28
pH @25°C | pH Units |  | SM 4500H | 07-Nov-18/O | 7.95 | 7.31
Conductivity @25°C | µmho/cm | 1 | SM 2510B | 07-Nov-18/O | 1180 | 671
TDS(ion sum calc.) | mg/L | 1 | Calc. | 13-Nov-18/O | 540 | 412
Total Suspended Solids | mg/L | 3 | SM2540D | 06-Nov-18/K | 230 | < 3
Turbidity | NTU | 0.1 | SM 2130 | 06-Nov-18/O | 25.2 | 0.3
Chloride | mg/L | 0.5 | SM4110C | 07-Nov-18/O | 56.2 | 56.6
Nitrite (N) | mg/L | 0.1 | SM4110C | 07-Nov-18/O | < 0.1 | < 0.1
Nitrate (N) | mg/L | 0.1 | SM4110C | 07-Nov-18/O | < 0.1 | 34.9
Sulphate | mg/L | 1 | SM4110C | 07-Nov-18/O | < 1 | 35
Aluminum | mg/L | 0.01 | SM 3120 | 13-Nov-18/O | 0.95 | 0.04
Arsenic | mg/L | 0.0005 | EPA 200.8 | 09-Nov-18/O | 0.001 | < 0.0005
Barium | mg/L | 0.001 | SM 3120 | 13-Nov-18/O | 0.03 | 0.017
Beryllium | mg/L | 0.002 | SM 3120 | 13-Nov-18/O | < 0.002 | < 0.002
Bismuth | mg/L | 0.02 | SM 3120 | 13-Nov-18/O | < 0.02 | < 0.02
Boron | mg/L | 0.005 | SM 3120 | 13-Nov-18/O | 0.13 | 0.14
Cadmium | mg/L | 0.005 | SM 3120 | 13-Nov-18/O | < 0.005 | < 0.005
Calcium | mg/L | 0.02 | SM 3120 | 13-Nov-18/O | 13.9 | 13
Chromium | mg/L | 0.002 | SM 3120 | 13-Nov-18/O | 0.003 | < 0.002
Cobalt | mg/L | 0.005 | SM 3120 | 13-Nov-18/O | < 0.005 | < 0.005
Copper | mg/L | 0.002 | SM 3120 | 13-Nov-18/O | 0.235 | 0.065
Iron | mg/L | 0.005 | SM 3120 | 13-Nov-18/O | 1.42 | 0.143
Lead | mg/L | 0.02 | SM 3120 | 13-Nov-18/O | < 0.02 | < 0.02
Lithium | mg/L | 0.01 | SM 3120 | 13-Nov-18/O | < 0.01 | < 0.01
Magnesium | mg/L | 0.02 | SM 3120 | 13-Nov-18/O | 5.3 | 4.93
Manganese | mg/L | 0.001 | SM 3120 | 13-Nov-18/O | 0.047 | 0.021
Mercury | mg/L | 2e-05 | SM 3112 B | 13-Nov-18/O | 0.00017 | < 0.00002
Molybdenum | mg/L | 0.01 | SM 3120 | 13-Nov-18/O | < 0.01 | < 0.01
Nickel | mg/L | 0.01 | SM 3120 | 13-Nov-18/O | < 0.01 | < 0.01
Silicon | mg/L | 0.01 | SM 3120 | 13-Nov-18/O | 2.09 | 2.01
Silver | mg/L | 0.005 | SM 3120 | 13-Nov-18/O | < 0.005 | < 0.005
Sodium | mg/L | 0.2 | SM 3120 | 13-Nov-18/O | 52.1 | 103
Zinc | mg/L | 0.005 | SM 3120 | 13-Nov-18/O | 0.286 | 0.09
Ammonia (N)-Total | mg/L | 0.01 | SM4500-NH3-H | 08-Nov-18/K | 109 | 0.07
Total Kjeldahl Nitrogen | mg/L | 0.1 | E3199A.1 | 07-Nov-18/K | 148 | 1.9
o-Phosphate (P) | mg/L | 0.01 | PE4500-S | 08-Nov-18/K | 11.1 | 9.66
Phosphorus-Total | mg/L | 0.01 | E3199A.1 | 07-Nov-18/K | 14.8 | 10.1
Phenolics | mg/L | 0.002 | MOEE 3179 | 09-Nov-18/K | 0.34 | 0.004
BOD(5 day) | mg/L | 3 | SM 5210B | 07-Nov-18/K | 382 | 4
COD | mg/L | 5 | SM 5220D | 07-Nov-18/O | 841 | 36
Dissolved Organic Carbon | mg/L | 0.2 | EPA 415.1 | 08-Nov-18/O | 81.7 | 14.9
Total Organic Carbon | mg/L | 0.2 | EPA 415.1 | 08-Nov-18/O | 84.8 | 19.9
Oil & Grease-Total | mg/L | 1 | SM 5520 | 06-Nov-18/K | 137 | < 1.0
Total Coliform | cfu/100mL | 1 | MOE E3371 | 05-Nov-18/O | 83000000 | < 10
E coli | cfu/100mL | 1 | MOE E3371 | 05-Nov-18/O | 2800000 | < 10
Fecal Strep. | cfu/100mL | 1 | MOE E3371 | 05-Nov-18/O | 47000 | < 10
Fecal Coliform | cfu/100mL | 1 | MOE E3371 | 05-Nov-18/O | 3600000 | < 10
Anion Sum | meq/L |  | Calc. | 13-Nov-18/O | 9.69 | 5.38
Cation Sum | meq/L |  | Calc. | 13-Nov-18/O | 11.8 | 6.26
% Difference | % |  | Calc. | 13-Nov-18/O | 9.9 | 7.57
Ion Ratio | AS/CS |  | Calc. | 13-Nov-18/O | 0.82 | 0.859
Sodium Adsorption Ratio | - |  | Calc. | 13-Nov-18/O | 3.01 | 6.17
Conductivity (calc.) | µmho/cm |  | Calc. | 13-Nov-18/O | 1160 | 660
TDS(calc.)/EC(actual) | - |  | Calc. | 13-Nov-18/O | 0.46 | 0.614
EC(calc.)/EC(actual) | - |  | Calc. | 13-Nov-18/O | 0.989 | 0.983
Langelier Index(25°C) | S.I. |  | Calc. | 13-Nov-18/O | 0.228 | -1.59

## B18-34755
Certificate of Analysis | [7 empty] | REPORT No. B18-34755
Final Report
Report To: |  |  |  |  | Caduceon Environmental Laboratories
Hamlet of Pangnirtung |  |  |  |  | 2378 Holly Lane
P.O. Box 253, |  |  |  |  | Ottawa Ontario K1V 7P1
Pangnirtung Nunavut X0A 0R0 Canada |  |  |  |  | Tel: 613-526-0123
Attention: | SAO - |  |  |  | Fax: 613-526-1244
DATE SUBMITTED: | 2018-11-09 11:47 |  |  |  | JOB/PROJECT NO.: |  | Waste Water
DATE REPORTED: | 2018-11-23 |  |  |  | P.O. NUMBER:
SAMPLE MATRIX: | Waste Water |  |  |  | WATERWORKS NO.:
|  |  | Client ID: |  | Pan 2 Influent | Pan 3 Effluent
|  |  | Sample ID: |  | B18-34755-1 | B18-34755-2
|  |  | Date Collected: |  | 05-Nov-18 | 05-Nov-18
Parameter | Units | M.D.L. | Reference Method | Date/Site Analyzed
Hardness (as CaCO3) | mg/L | 1 | SM 3120 | 19-Nov-18/O | 60 | 76
Alkalinity(CaCO3) to pH4.5 | mg/L | 5 | SM 2320B | 12-Nov-18/O | 689 | < 5
pH @25°C | pH Units |  | SM 4500H | 12-Nov-18/O | 8.7 | 5.97
Conductivity @25°C | µmho/cm | 1 | SM 2510B | 12-Nov-18/O | 1610 | 682
TDS(ion sum calc.) | mg/L | 1 | Calc. | 19-Nov-18/O | 790 | 411
Total Suspended Solids | mg/L | 3 | SM2540D | 13-Nov-18/K | 480 | < 3
Turbidity | NTU | 0.1 | SM 2130 | 15-Nov-18/O | 355 | 0.3
Chloride | mg/L | 0.5 | SM4110C | 13-Nov-18/O | 58.7 | 106
Nitrite (N) | mg/L | 0.1 | SM4110C | 13-Nov-18/O | < 0.1 | < 0.1
Nitrate (N) | mg/L | 0.1 | SM4110C | 13-Nov-18/O | < 0.1 | 23.3
Sulphate | mg/L | 1 | SM4110C | 13-Nov-18/O | 9 | 39
Aluminum | mg/L | 0.01 | SM 3120 | 19-Nov-18/O | 1.19 | 0.08
Arsenic | mg/L | 0.0005 | EPA 200.8 | 12-Nov-18/O | 0.0009 | < 0.0005
Barium | mg/L | 0.001 | SM 3120 | 19-Nov-18/O | 0.196 | 0.179
Beryllium | mg/L | 0.002 | SM 3120 | 19-Nov-18/O | 0.028 | 0.02
Bismuth | mg/L | 0.02 | SM 3120 | 19-Nov-18/O | < 0.02 | < 0.02
Boron | mg/L | 0.005 | SM 3120 | 19-Nov-18/O | 0.192 | 0.18
Cadmium | mg/L | 0.005 | SM 3120 | 19-Nov-18/O | < 0.005 | < 0.005
Calcium | mg/L | 0.02 | SM 3120 | 19-Nov-18/O | 14.7 | 20
Chromium | mg/L | 0.002 | SM 3120 | 19-Nov-18/O | 0.005 | 0.004
Cobalt | mg/L | 0.005 | SM 3120 | 19-Nov-18/O | < 0.005 | < 0.005
Copper | mg/L | 0.002 | SM 3120 | 19-Nov-18/O | 0.274 | 0.118
Iron | mg/L | 0.005 | SM 3120 | 19-Nov-18/O | 1.72 | 0.175
Lead | mg/L | 0.02 | SM 3120 | 19-Nov-18/O | < 0.02 | < 0.02
Lithium | mg/L | 0.01 | SM 3120 | 19-Nov-18/O | < 0.01 | < 0.01
Magnesium | mg/L | 0.02 | SM 3120 | 19-Nov-18/O | 5.69 | 6.25
Manganese | mg/L | 0.001 | SM 3120 | 19-Nov-18/O | 0.057 | 0.097
Mercury | mg/L | 2e-05 | SM 3112 B | 19-Nov-18/O | 0.00025 | < 0.00002
Molybdenum | mg/L | 0.01 | SM 3120 | 19-Nov-18/O | < 0.01 | < 0.01
Nickel | mg/L | 0.01 | SM 3120 | 19-Nov-18/O | < 0.01 | < 0.01
Silicon | mg/L | 0.01 | SM 3120 | 19-Nov-18/O | 2.53 | 3.06
Silver | mg/L | 0.005 | SM 3120 | 19-Nov-18/O | < 0.005 | < 0.005
Sodium | mg/L | 0.2 | SM 3120 | 19-Nov-18/O | 237 | 104
Zinc | mg/L | 0.005 | SM 3120 | 19-Nov-18/O | 0.398 | 0.366
Ammonia (N)-Total | mg/L | 0.01 | SM4500-NH3-H | 14-Nov-18/K | 10.3 | 0.1
Total Kjeldahl Nitrogen | mg/L | 0.1 | E3199A.1 | 12-Nov-18/K | 138 | 1.6
o-Phosphate (P) | mg/L | 0.01 | PE4500-S | 13-Nov-18/K | 12.3 | 10.2
Phosphorus-Total | mg/L | 0.01 | E3199A.1 | 12-Nov-18/K | 14.2 | 11.5
Phenolics | mg/L | 0.002 | MOEE 3179 | 14-Nov-18/K | 0.285 | < 0.002
BOD(5 day) | mg/L | 3 | SM 5210B | 12-Nov-18/K | 930 | 3
COD | mg/L | 5 | SM 5220D | 13-Nov-18/O | 1160 | 41
Dissolved Organic Carbon | mg/L | 0.2 | EPA 415.1 | 12-Nov-18/O | 142 | 11.2
Total Organic Carbon | mg/L | 0.2 | EPA 415.1 | 12-Nov-18/O | 153 | 16
Oil & Grease-Total | mg/L | 1 | SM 5520 | 15-Nov-18/K | 76.9 | < 1.0
Total Coliform | cfu/100mL | 1 | MOE E3371 | 09-Nov-18/O | 90000000 | 1800000
E coli | cfu/100mL | 1 | MOE E3371 | 09-Nov-18/O | 7200000 | < 2
Fecal Strep. | cfu/100mL | 1 | MOE E3371 | 09-Nov-18/O | 1700000 | 2
Fecal Coliform | cfu/100mL | 1 | MOE E3371 | 09-Nov-18/O | 9900000 | 80
Anion Sum | meq/L |  | Calc. | 19-Nov-18/O | 15.9 | 5.53
Cation Sum | meq/L |  | Calc. | 19-Nov-18/O | 13.1 | 6.83
% Difference | % |  | Calc. | 19-Nov-18/O | 9.57 | 10.5
Ion Ratio | AS/CS |  | Calc. | 19-Nov-18/O | 1.21 | 0.809
Sodium Adsorption Ratio | - |  | Calc. | 19-Nov-18/O | 13.3 | 5.2
Conductivity (calc.) | µmho/cm |  | Calc. | 19-Nov-18/O | 1280 | 713
TDS(calc.)/EC(actual) | - |  | Calc. | 19-Nov-18/O | 0.49 | 0.602
EC(calc.)/EC(actual) | - |  | Calc. | 19-Nov-18/O | 0.794 | 1.05
Langelier Index(25°C) | S.I. |  | Calc. | 19-Nov-18/O | 1.22 | -3.64