## Sheet1
Calculation of annual water extraction from Char Lake
| Year | 2020 | 2030 | 2047
Population | Persons | 290 | 317.7778 | 365
Community Per Capita Consumption | L/capita/day | 225 | 232 | 243.9
Community Consumption | L/day | 65250 | 73724.4444 | 89000
Airport Consumption (based on approx 140L/c/d) | L/day | 38100 | 43248.1481 | 52000
Total Consumption | L/day | 103350 | 116972.5926 | 141000
Total Consumption (based on max day factor 2.75) | L/day | 284212.5 | 321674.6296 | 387750
Total Consumption (based on max day factor 2.75) | L/s | 3.2895 | 3.7231 | 4.4878
Bleedwater | L/day | 155520 | 193920 | 259200
Community Wide Demand | L/day | 439732.5 | 515594.6296 | 646950
Community Wide Demand | m3/day | 439.7325 | 515.5946 | 646.95
Community Wide Demand | L/s | 5.0895 | 5.9675 | 7.4878
Annual Consumption | Liters | 160502362.5 | 188192039.8148 | 236136750
Annual Consumption | m3 | 160502.3625 | 188192.0398 | 236136.75