## Slide 1: PRESENTATION FOR THE TYPE A WATER LICENCE APPLICATION OF THE RESOLUTE BAY UTILIDOR SYTEM NWB TECHNICAL MEETING AND PRE-HEARING CONFERENCE OVER PHONE JULY 14 AND JULY 15, 2020 PRESENTED BY: BHABESH ROY, M.A.Sc., P.Eng. MUNICIPAL PLANNING ENGINEER COMMUNITY GOVERNMENT SERVICES GOVERNMENT OF NUNAVUT BAFFIN REGION, POND INLET BOX 379, X0A 0S0, NUNAVUT PH. 867 899 7314, Cell 867 899 1345

## Slide 2: MUNICIPALITY OF RESOLUTE BAY
The early 1970, the settlement was moved to the present location at N 74043’01’’ and W 94058’10”. The Relocated Community , Municipality of Resolute Bay, was designed to accommodate 1500 people.
The Current basic Town population in 2020 is 288 . During summer, due to Military presence for training, The population of the Town is raised sometimes to about 800.
The town is divided into two sections:
The main Town where water is supplied by the Utilidor system
The Airport area about 7km away where water is supplied by the Truck.
NWB has issued three Water Licences for the three different Environmental facilities of the Community.
The Water Licence of the Utilidor System #3BM-RUT1012, Type B was issued on March 30, 2015 to the Department of Community Government Services of the Government of Nunavut.
The Water Licence of the Solid wastes facilities # 3BM-RES 2025,Type B was issued on March 30,2020 to the Municipality of Resolute Bay.
The Water Licence of the Airport Sewage Lagoon # 3BM-YRB 1621, Type B was issued on Dec.16,2016 to the Department of Economic Development and Transportation of the Government of Nunavut.

## Slide 3: OPERATIONAL MODE OF THE UTILODOR SYTEM
The Asset Management section of the Pond Inlet Infrastructure Division of the Government of Nunavut is Responsible for the Utilidor system. This facility was contacted out to ATCO for the day to day operation.
Char Lake is the Potable water Source and a pump station is existing at the bank of the Lake. A new pump station about 50m away from the existing pump station is under construction at present. The flow meter located at the existing pump station records water extraction volume from the Char Lake. The new Pump station will have its new flow meter.
The Water Treatment Plant (WTP) is located at the Signal Hill and a Storage Tank is also there next to the Plant.
The Water Truck is filled directly at the WTP for the distribution to the Airport facilities.
The Water distribution system must have a circulation pattern that is independent of and unaltered by demands, other than Fire flows. This system is controlled from the WTP.
Chlorine is only the reagent to disinfect water inside of the WTP prior to distribution.
contd:

## Slide 4: OPERATIONAL MODE OF THE UTILIDOR SYSTEM
The linear length of the Utilidor system is about 4 km.
The Utilidor system consists of a water line and a sewer line and both lines are buried.
The Diameter of the water line is 150mm and sewer line is 200mm,
The Water line is a recirculation process and works under about 100 psi pressure system ; whereas the sewer line is completely under gravity system adding bleeding water.
The estimated bleeding water is roughly 227 Litres per day or 82,944 litres annually.
The Utilidor system consists of 36 Access Vaults and 23 Fire hydrants.
There is a water meter at each building to record water consumption.
The sewer line passes through the Macerator unit where suspended solids are grinded into smaller particles to discharge into the sea.
A new wastewater treatment plant (WWTP) is proposed to be built at the side of the existing Macerator unit. This Macerator unit will be decommissioned soon after the new WWTP is commissioned.
The future WWTP will receive Truck Sewage and the mixture of the both types of sewages will be treated at the new WWTP.
The CBOD and TSS of the future WWTP effluent are recommended to be 25mg/l and 25mg/L respectively.

## Slide 5: TYPE A WATER LICENCE APPLICATION OF THE MUNICIPALITY OF RESOLUTE BAY UTILITOR SYTEM
STATUS OF THE EXISTING WATER LICENCE:
EXISTING WATER LICENCE # 3BM-RUT 1012
LICENSEE: COMMUNITY GOVERNMENT SERVICES OF THE GOVERNMENT OF NUNAVUT
TYPE: TYPE B
DATE OF ISSUSE: MARCH 30,2015
DATE OF EXPIRE: MARCH 29,2020
DURATION: 5 YRS
WATER PERMIT VOLUME:126,020 CUBIC METERS
STATUS OF THE PROPOSED WATER LICENCE
PROPOSED WATER LICENCE # 3AM-RUT--------
LICENSEE: COMMUNITY GOVERNMENT SERVICES OF THE GOVERNMENT OF NUNAVUT
PROPOSED TYPE: TYPE A
PROPOSED DURATION: 10 YEARS
PROPOSED WATER PERMIT VOLUME: 150,000 CIBIC METERS

## Slide 6: DESCRIPTION OF UTILIDOR SYTEM
THE COMPONENTS OF THE EXISTING UTILIDOR SYSTEM
THE BURIED WATER AND SEWER LINES: 4KM
FIRE HYDRANTS: 23 NOS.
ACCESS VAULTS= 36 NOS.
A PUMP STATION AT CHAR LAKE
A WATER STORGAE TANK AT SIGNAL HILL: 4000 CUBIC METRES
A WATER TREATMENT PLANT AT SIGNAL HILL
MACERATOR UNIT ( NO FLOW METER AND GRINDING UNIT EXIST)
A 150 MM DIAMETER WTAER INTKE LINE FROM CHARLAKE TO PUMP STATION
A 150 MM DIAMETER WATER INTAKE LINE FROM PUMP STATION TO SIGNAL HILL WATER PLANT
A 200 MM DIAMETER OUTFALL LINE FROM MACERATOR UNIT TO SEA
THE ENTIRE UTILIDOR SYSTEM WAS BUILT IN 1978

## Slide 7: COMPONENTS OF THE FUTURE UTILIDOR SYSTEM
STATUS
THE MAIN BURIED WATER AND SEWER LINES ( Main Utilidor System) : UPGRADED
VAULTS: UPGRADED
FIRE HYDRANTS: UPGRADED
AN INTKE FROM THE CHARLAKE TO NEW PUMP STATION: UNDER CONSTRUCTION
FISH SCREEN WILL BE PROVIED AT THE END OF THE INTAKE
A NEW PUMP STATION AT SIGNAL HILL: UNDER CONSTRUCTION
A STANDARD FLOW METER WILL BE INSTALLED AT THE NEW PUMP STATION
INTAKE FROM NEW PUMP STATION TO SIGNAL HILL WATER TREATMENT PLANT :
CONSTRUCTED
7. A STORAGE TANK AT SIGNAL HILL: CONSTRUCTED
8. A NEW WASTEWATER TREATMENT PLANT: FUTURE CONSTRUCTION
9. A NEW OUTFALL FROM WWTP TO THE SEA : FUTURE CONSTRUCTION
10: A COLLECTION POINT AT WWTP TO RECEIVE TRUCK SEWAGE: FUTURE CONSTRUCTION
11. THE OLD PUMP STATION, MACERATOR UMIT, OUTFALL LINE AND OLD WWTP BUILDING: FUTURE DECOMMISSIONING

## Slide 8: THE UTILIDOR SYSTEM OF THE MUNICIPALITY OF RESOLUTE BAY
Char Lake
New Pump House
Existing Pump Station
New Intake(Pressure pipe)
Old intake (Pressure Pipe)
Storage tank
SIGNAL HILL
Water Treatment Plant
MUNICIPALITY OF RESOLUTE BAY
Macerator Unit
SEA
Compliance Point
Water Distribution and Sewer Line
Truck Disposal Point
New Wastewater Treatment Plant
Outfall line (Sewer line under Gravity)

## Slide 9: HISTORICAL WATER EXTRACTION VOLUME
Trucking to
Year Utilidor System (litres) Airport Facilities (Litres) Total Extraction (litres)
2019 191,355,032 5,454,865 197,809,897
2018 152,062,035 5,139,821 157,201,856
2017 127,669,936 5,351, 523 123,121, 459
2016 326,439,020 5,351,523 331,790, 543
2015 424,262,506 4,210,285 428,472,791
2014 110,202,314 4,749,032 114,951,346
Permit Volume in Water Licence annually = 126,020 cubic metres=126,020,000Litres.
Proposed Volume in the New Water Licence=150,000 cubic meters=150,000,000 Litres
Daily extraction exceeds 300cubic meter per day. Therefore, the type of the new Water
Licence is recommended as TYPE A.

## Slide 10: RESOLUTE BAY POPULATION (Exp’s Pre-design Report 2012)
Town site Area:
YEAR POPULATION
2017 273
2022 288
2027 302
2032 316
2037 330
2042 347
2047 365
Airport Area:
Airport Facilities= 40
Polar Continental Self= about 200
DND Arctic Training Centre= Variable
New hotel= 30

## Slide 11: CONSTRUCTION STRATEGY OF THE NEW PUMP STATION
FOLLOW THE ENVIRONMENTAL MANAGEMENT PLAN
FOLLOW THE WORKPLACE HEALTH AND SAFETY PROTOCOL
MAINTAIN THE CHAR LAKE WATER QUALITY SAFE
SATISFY THE DFO’S REQUIRENTS FOR FISH SCREEN AT THE END OF THE INTAKE
INSTAL A NEW FLOW METER TO RECORD THE EXTRACTION VOLUME OF WATER FROM THE CHAR LAKE ON DAILY BASIS.
HYDRAULIC TEST PRIOR TO COMMISSIONING THE INTAKE
THE PROVISION OF THE EMERGENCY BYPASS

## Slide 12: MANAGEMENT OF LATERAL CONNECTIONS
LATERAL MAIN DOES NOT FALL UNDER THE UTILIDOR CONTRACT
EACH LATERAL MAIN IS ABOUT 30 TO 35 M LONG
THE MAINTENANCE OF THE LATERAL MAIN IS THE RESPONSIBILTY OF THE INDIVIDUAL HOUSE OWNER. IN OTHERWORS HOUSING CORPORATION.
ANY EMERGENCY OF THE LATERAL MAIN , SHOULD CONTACT:
RESOLUTE BAY HOUSING CORPORATION.
ATCO OFFICE IN RESOLUTE BAY COULD BE CONSULTED AS WELL.
Phone: 867 252 3737 and e-mail: Philip.chubbs@atco.ca and Richard.gaulton@atco.ca

## Slide 13: DESIGN WATER DEMANDS AND SEWAGE GENERATION Exp’s Pre-Design Report 2012
YEAR DESIGN WATER DEMANDs DESIGN SEWAGE FLOWS
(Inclusive of bleed water Flows) (Inclusive of Bleed water Flows)
Community Maximum Hour, L/S Peak Flow , L/S
2017 6.1 6.0
2022 6.7 6.6
2027 7.1 7.0
2032 7.6 7.5
2037 8.0 7.9
2042 8.5 8.4
2047 9.0 8.9
Note: Bleed water requirements are estimated as 1.8L/s, maximum 3.0L/s for the future extension of the sewer lines.

## Slide 14: ECCC RECOMMENDED WASTEWATER EFFLUENT COMPLIANCY
Average Carbonaceous Biochemical Oxygen Demand (CBOD) should be less than or equal to 25mg/L.
Average concentration of suspended solids should be less than or equal to 25mg/L
Average Concentration of the Total residual chlorine should be less than or equal to 0.02mg/L
Maximum concentration of un-ionized ammonia should be less than 1.25mg/L expressed as Nitrogen (N), at 150C +/- 10C
Be non-accurately lethal effluent

## Slide 15: SCHEDULING OF THE TECHNICAL MEETING AND PRE- HEARING CONFERENCE
TECHNICAL MEETING:
DATE: JULY 14, 2020
TIME: 8.00AM to 3.00PM (MT)
VIRTUAL: Toll Free number: 1-888-289-4573 ; Access Code: 7270413
PRE-HEARING CONFERENCE:
DATE: JULY 15, 2020
TIME: 8.00 AM to 3.00PM (MT)
VIRTUAL: Toll Free Number: 1-888-289-4573: Access Code: 7270413

## Slide 16: PARTICIPANTS FOR THE TM/PHC OVER PHONE
GN LICENCE REPRESENTATIVE:
BHABESH ROY, M.A.Sc., P.Eng.: MUNICIPAL PLANNING ENGINEER,
BAFFIN REGION, POND INLET:
CONTACT PERSON: 867 899 7314, cell 867 899 1345 and e-mail: broy@gov.nu.ca
ATCO:
PHILIP CHUBBS , MANAGER OR RESOLUTE BAY OPERATION
PH: 867 252 3737 and e mail: Philip.chubbs@atco.ca
AND RICHARD GAULTON , SPERINDENDENT OF THE RESOLUTE BAY OPERATION
Ph: 867 252 3737 and e mail; Richard.gaulton@atco.ca
MUNICIPALITY OF RESOLUTE BAY:
STEVEN , CAO, Ph: 867 252- 3832 and e mail: sao@resolute.ca
THE CONSULTANT:
EXP SERVICES INC:

## Slide 17: LOCATIONS OF THE IMPORTANT FACILITIES OF THE MUNICIPALITY OF RESOLUTE BAY