2017 ANNUAL REPORT


FOR THE HAMLET OF RESOLUTE BAY, NUNAVUT

ANNUAL REPORT


FOR THE HAMLET OF RESOLUTE BAY, NUNAVUT

2017 ANNUAL REPORT


FOR THE HAMLET OF RESOLUTE BAY, NUNAVUT


YEAR BEING REPORTED: 2017 Utilidor


The following information is compiled pursuant to the requirements of Part B, Item 1 of Water License # 3BM-RUT1520 issued to the Hamlet of Resolute Bay, Nunavut.
i) - iii)
tabular summaries of all data generated under the “Monitoring Program”; monthly and annual quantities in cubic metres of freshwater obtained from all sources; monthly and annual quantities in cubic metres of each and all wastes discharged;

Attached are quantities of water used as reported in our On Tap Water Delivery System and the estimated discharge of sewage waste based on quantities used.
	Month Reported
	Quantity of Water Obtained from all sources (litres)
	Quantity of Sewage Waste Discharged
(Estimated)

	January
	12,864,745
	Same

	February
	9,968,797
	Same

	March
	10,400,690
	Same

	April
	12,357,150
	Same

	May
	11,713,727
	Same

	June
	9,823,936
	Same

	July
	9,663,013
	Same

	August
	9,779,248
	Same

	September
	9,266,479
	Same

	October
	10,369,813
	Same

	November
	9,917,872
	Same

	December
	11,544,466
	Same

	Annual Total
	127,669,936
	Same


      Note: The extraction volume used for the Utilidor system is considered equal to the  

     discharge volume in each month because there is no meter in the sewer discharge pipe.
The total extraction volume from the Char Lake is divided into Utilidor system by liner system

             and to the Airport facilities by truck delivery. The Utilidor consumes 127,669,936 litres and the rest is for trucking 5,173,917 litres. Total extraction volume was 132,843,853 litres.
iv. A summary of modifications and/or major maintenance work carried out on the Water Supply and Waste Disposal Facilities, including all associated structures and facilities;




The entire Utilidor system including buried pipes and valves has been rehabilitated and it is now functioning well. No leakage is observed. No loss of water due to leaking or flooding is observed at present. The water extraction volume from the Char Lake and the associated cost has significantly been reduced.
          ___________________________________________________________________
v. A list of unauthorized discharges and summary of follow-up action taken;    



The Utilidor system runs without a WWTP. The Macerator unit located at the lower part of the sewer line is about 500m from the sea shore crushes the suspended solids at certain degree. Also in absence of a WWTP, sewage is highly diluted and runs into the sea without any further treatment.

vi. A summary of any abandonment and restoration work completed during the year and an outline of any work anticipated for the next year; 



All the fire Hydrants and Valves were replaced along with the liner system. 
 The Macerator unit will not be required any more once the new WWTP is built and commissioned. The existing Pump house at Char Lake is planned to be decommissioned only if the new one is built and commissioned next year. 
            ________________________________________________________________ 
vii. A summary of any studies requested by the Board that relate to waste disposal, water use or reclamation, and a brief description of any future studies planned;

______________________________________________________________________

                  The design works for the new Pump station and decommissioning of the existing 

                  Pump station at Char Lake are completed. The design for upgrading the Signal Hill 

                  WTP is in progress.
                  A Study was conducted on the sewage effluent quality last summer by exp Services 

                   Inc. and the report were submitted to NWB. This study was the requirement of the 

                  Water Licence compliancy.
           __________________________________________________________________

viii. Any other details on water use or waste disposal requested by the Board by November 1st of the year being reported; and


                    The Licensee conducted a site specific study for the determination of a Fecal 
                    Coliform limit for Sewage Disposal Facility during the last summer.

                    The Report is attached.
           ______________________________________________________________________

ix. Updates or revisions to the approved Operation and Maintenance Plans.

     ________________________________________________________________  

The Phase 1 Liner system construction was completed. The O&M manual was updated and submitted to NWB. Individual O&Ms will be prepared for the Char Lake new pump station and the WTP at signal Hill once their construction is completed.
           _____________________________________________________________________

     x.       ADDITIONAL INFORMATION THAT THE LICENSEE DEEMS USEFUL:

                    GN-CGS contacted out this facility to ATCO for daily maintenance. They are 
                 operating this system and maintaining water quality for the safety of the public health 
                 and to comply with the requirements of the Water Licence. The Utilidor Water Licence 

                 is in the amendment process to approve the design of the Char Lake new pump station                   in order to start  construction soon.

    xi.          FOLLOW-UP REGARDING INSPECTION/COMPLIANCE CONCERNS:


                  GN-CGS is the owner and Licensee of the Utilidor system.  GN-CGS is working closely 
               with the Water Licence Compliance Group (WLCG) and receiving direction to move 
               forward in order to renew or amend the Utilidor water licence.

               

             The Lab Test results for 2017 are attached in a different document.
