## Sheet1
Comparison of the Revised O&M Manual of 2010 versus 2007
P Lake Sewage Lagoon: Cape Dorset
Revised O&M Manual 2010 | Original O&M manual 2007
This is a revised O&M manual of May 2010 | The original manual was presented by Dillon
which is based on the manual updated by | consulting Ltd in November 9,2007.
Dillon Consulting Ltd in Sep.3, 2009 from their
Basic document of November 9, 2007.
Item 2.1.1 has been revised adding Appendix- | The original document missed appendix-A in page
A in page 4. Page #6 has been changed with an | # 4. This was not the as -built shown thermistors
as built drawing showing exact locations of | locations in page # 6 because at that time thermistor
the thermistors.This drawing has been signed | issues were not discussed and considered.
and stamped by the Engineer of Dillon.
Item 3.4.1, Basic Operation, page #8 : CAP-3 is | Item 3.4.1, Page 8 : table 3 is there but its contents
changed to CAP-4 and CAP-4 is changed to | are different . Item 3.4.3 not acceptable.
CAP-5. Table 3 and 4 are added. Also item
3.4.3 is revised at page 10.
Item3.4.4.page 10: Fecal Coliforms, FC 1.5*104 | Item 3.4.4, is not acceptable.
FCU/100mL which the consultant has
considered in their design. The consultant feels
their design value should stand. The write up of
the entire item has been revised.
Item 3.4.4 page 14, second to last paragraph: first | Item 3.4.4, Page 12: one year of operation.
two years of operation.
3.4.5: Monitoring wells were constructed in June, | This was not an issue at that time when the document
2011 | was prepared. Therefore this item was not there.
Item 3.4.5: Ground Monitoring wells is added. | Ground Monititoring wells were not there.
Item3.4.6: Sludge monitoring plan is revised. | Item 3.4.5 sludge management plan was not acceptable.
Item 3.4.7: Geothermal Monitoring is revised. | Item 3.4.5 Geothermal monitoring Plan was not acceptable.
3.4.7: This is a new item developed once License | In this initial document, this information was not there
was issued in March 7,2008. Thermistors were | because it was not an issue.
constructed and GPS coordinates have been
established and shown in item 3.4.7. page 16 in
table 7.
As-built drawings were signed by Dillon in 2009 | Item, 3.4.8 of page 14: Record keeping and reporting were
is included in page 17. Also item 3.4.9 of page 19 | not acceptable.
is revised.
Item 4.0: Spill Contingency Plan is entirely revised. | Item 4.0 page 6 was not acceptable.
Item 5.0: Response organization: Added new | This was not included.
chapter.
Item 6: Added new Chapter | This was not included.
Item 7: Resource inventory: Added new Chapter | This was not included.
As built drawings: Only one drawing shows | All the as-built drawing except site plan are correct and
thermistor locations has been changed. | unchanged as per Dillon Consulting Ltd.
Addition of new O&M manual for Monitoring Wells | This was not an issue and not included in the original manual.