Water Licence 3BM-CLY1924 Renewal and Amendment Application: Amendment Justification Summary

Government of Nunavut

Community and Government Services

October 17, 2024

The Municipality of Clyde River is applying to renew and amend Water Licence 3BM-CLY1924. The amendments the Municipality would like to apply as well as justification are as presented in Table 1. The proposed amendments are to ensure the municipal water use demands are sufficiently met through to 2044, to align the licence with newly issued municipal licences requirements that are based on evidence and best practices, and to remove previous requirements that are no longer relevant or practical.

Table 1. Proposed Amendments to Municipality of Clyde River Renewed Water Licence

| ITEM | REQUEST | JUSTIFICATION |
| --- | --- | --- |
| All applicable items | Change term “Hamlet” to “Municipality” | Municipality is the preferred term by the Licensee. |
| B-1-d | Remove requirement to report daily quantities in cubic metres of sewage and solid waste discharged. Change from daily to monthly and annually. | It is not practical to report daily sewage and solid waste quantities in the annual report, unless NWB finds that an estimate calculated from the monthly and annual amounts is acceptable. The Licensee requests that this condition be modified to monthly and annual sewage quantities, and annual solid waste quantities. There is currently no solid waste attendant position funded in the municipal budget to support daily and monthly solid waste reporting. As per Water Licence 3BM-ARC1924, the requirement is monthly and annually for sewage and solid waste discharge quantities. |
| B-7 | Remove municipal boundaries from the requirement and change requirement from “in the areas of the Water Supply or Waste Disposal Facilities” to spills related to Licenced Facilities. | Only spills related to the operation of Licenced Facilities should follow this requirement for this municipal water licence. There are spills within the municipal boundaries that are intended to be dealt with by agencies such as QEC and NHC, who are not authorized licensees under the municipal water licence. |
| C-2 & Quantity of Water use not to Exceed – Annum | Increase from 59,900 cubic metres per annum to 72,000 cubic metres per annum | It is expected that 72,000 m3 will be sufficient to supply the municipality until at least 2044. The population and consumption projections are presented in the table below: Parameter; Value. 2023 Population*; 1278. Projected Annual Growth Rate to 2043 (%)*; 1.1. Projected 2044 Population; 1575. Consumption Rate (L/d/capita)**; 120. 2044 Annual Water Use (m3); 68,985. *Nunavut Bureau of Statistics **Government of Nunavut Standard Water Treatment Train |
| C-3 | Remove requirement | A hydrological study will be conducted on Water Source Lake during summer 2025 to determine the viability of the Water Source Lake as the municipal water source for the upcoming decades. The report will be provided in the 2025 Annual Report submission. |
| D-2 | Amend the effluent compliance point from CLY-4 and CLY-5 to CLY-6b | The Wastewater Treatment Facility is designed as a lagoon-wetland treatment system for which the wetland performs significant effluent treatment based on the lab results from the Water Licence monitoring program. The end of the wetland is where the effluent enters the receiving environment and should therefore be the compliance point, as it represents the fully treated effluent. |
|  | Amend the parameter BOD5 to cBOD with a 100 mg/L maximum concentration of any grab sample Amend the maximum concentration of any grab sample of 120 mg/L for total suspended solids | cBOD is replacing BOD5 as the standard test parameter as indicated in Good Engineering Practice for Northern Water and Sewer Systems, Government of Northwest Territories, 2017. These limits can be reliably met by lagoon-wetland systems while preserving the health of the receiving environment as demonstrated during multi-year Nunavut research conducted by the Centre for Water Resource Studies at Dalhousie University. The findings were recommended by EXP in the Recommendations for the Development of Nunavut Municipal Wastewater Management Standards, 2017. |
| F-1 | Remove requirement as the Plan is no longer a standalone document. | The procedures from the Plan entitled “Hazardous Waste Segregation, Storage and Transportation Procedure” dated July 2019 have been transferred over and updated in the new operations and maintenance Plan for the solid waste facility entitled "Municipality of Clyde Operation & Maintenance Plan for Municipal Water Licence: Solid Waste Disposal Facilities" dated November 2024, which is updated to the standardized template approved by the Board. |
| F-2 | Amend to most recent manual | The operations and maintenance manual for spill contingency was updated to the standard template entitled “Municipality of Clyde River Environmental Emergency Contingency Plan for Municipal Water Licence" dated November 2024. |
| F-3 | Amend to most recent manual | The operations and maintenance manual for the water supply facility was updated to the standard template entitled “Municipality of Clyde River Operation & Maintenance Plan for Municipal Water Licence: Water Supply Facilities" dated November 2024. |
| F-4 | Amend to most recent manual | The operations and maintenance manual for the solid waste facility was updated to the standard template entitled “Municipality of Clyde River Operation & Maintenance Plan for Municipal Water Licence: Solid Waste Disposal Facilities" dated November 2024. |
| F-5 | Amend requirement for the Engineer’s inspection report to be submitted within sixty (60) days of the inspection | Final reports typically take longer than 60-days to be received from a consultant and reviewed by the technical team. The licensee requests that the submission timeline be adjusted to 60 days after the final report is submitted by the consultant. |
| F-7-a | Amend to most recent manual | The operations and maintenance manual for spill contingency was updated to the standard template entitled “Municipality of Clyde River Environmental Emergency Contingency Plan for Municipal Water Licence" dated November 2024. |
| H-1 | CLY-6a remove from monitoring program | Sampling from CLY-6a is redundant as the monitoring program includes surface water samples from the same location at CLY-6b. |
|  | CLY-9, CLY-10, and CLY-11 remove from monitoring program | CGS has contracted Dillon to study the recommended frequency of an engineer’s inspection of the water and waste infrastructure including the Clyde River sewage lagoon. The findings of the study will be provided in the 2024 annual report to request a defensible inspection and monitoring method and frequency. |
|  | CLY-12 remove from monitoring program | According to the Operations and Maintenance Manual for the Wastewater Treatment Facility Hamlet of Clyde River: “it is recommended that settlements of the berms should be monitored for 2 to 3 years subsequent to completion of construction” (EXP, 2012). The sewage lagoon was constructed in 2011. Monitoring settlement is no longer relevant. CGS has contracted Dillon to study the recommended frequency of an engineer’s inspection of the water and waste infrastructure including the Clyde River sewage lagoon. The findings of the study will be provided in the 2024 annual report to request a defensible inspection and monitoring method and frequency. |
| H-3 | Remove requirement to measure and record daily, monthly, and annual quantities in cubic metres of sewage discharged. | It is not practical to measure and record the quantities of effluent pumped as there is no inline flowmeter for the sewage discharge piping. For truck-lagoon wastewater systems, it is normally estimated that the volume of sewage discharged during the open water season is equal to the amount of water withdrawn from the water source (CLY-1). The daily, monthly, and annual sewage effluent discharge quantities can be estimated only by assuming the amount of sewage at CLY-4 and CLY-5 is equal to CLY-1 and the volume per period (daily, monthly, annually) calculated based on the number of days which sewage was pumped from the lagoons. The Licensee requests that this condition be modified to recording sewage effluent discharge quantities based on an estimate using CLY-1 and the number of days of pumping rather than by direct measurement. |
| H-4 | Remove requirement to sample at monitoring station CLY-6a | Sampling from CLY-6a is redundant as the monitoring program includes surface water samples from the same location at CLY-6b. |
| H-8 | Amend to most recent manual | CGS has contracted Dillon to study the recommended frequency of an engineer’s inspection of the water and waste infrastructure including the Clyde River sewage lagoon. The findings of the study will be provided in the 2024 annual report to request a defensible inspection and monitoring method and frequency. |
| H-9 | Remove requirement | CGS has contracted Dillon to study the recommended frequency of an engineer’s inspection of the water and waste infrastructure including the Clyde River sewage lagoon. The findings of the study will be provided in the 2024 annual report to request a defensible inspection and monitoring method and frequency. |
| H-10 | Remove requirement | CGS has contracted Dillon to study the recommended frequency of an engineer’s inspection of the water and waste infrastructure including the Clyde River sewage lagoon. The findings of the study will be provided in the 2024 annual report to request a defensible inspection and monitoring method and frequency. |
| H-11 | Remove requirement | According to the Operations and Maintenance Manual for the Wastewater Treatment Facility Hamlet of Clyde River: “it is recommended that settlements of the berms should be monitored for 2 to 3 years subsequent to completion of construction” (EXP, 2012). The sewage lagoon was constructed in 2011. Monitoring settlement is no longer relevant. CGS has contracted Dillon to study the recommended frequency of an engineer’s inspection of the water and waste infrastructure including the Clyde River sewage lagoon. The findings of the study will be provided in the 2024 annual report to request a defensible inspection and monitoring method and frequency. |
| H-12 | Remove requirement | According to the Operations and Maintenance Manual for the Wastewater Treatment Facility Hamlet of Clyde River: “it is recommended that settlements of the berms should be monitored for 2 to 3 years subsequent to completion of construction” (EXP, 2012). The sewage lagoon was constructed in 2011. Monitoring settlement is no longer relevant. CGS has contracted Dillon to study the recommended frequency of an engineer’s inspection of the water and waste infrastructure including the Clyde River sewage lagoon. The findings of the study will be provided in the 2024 annual report to request a defensible inspection and monitoring method and frequency. |