## B18-10510
Raw water Chemical Analysis of the Primary and Secondary Water Sources of the Municipality of Grise Fiord
Report To: |  |  | Caduceon Environmental Laboratories
Hamlet of Grise Fiord |  |  | 2378 Holly Lane
P.O. Box 77 Grise Fiord, |  |  | Ottawa Ontario K1V 7P1
Grise Fiord NU X0X 0J0 |  |  | Tel: 613-526-0123, Fax: 613-526-1244
|  |  | 2018 | 2017 | 2017 | 2016 | 2016 | 2015
Parameters | Units | M.D.L. | Primary Source | Primary Source | Seconadry Source | Seconadry Source | Primary source | Primary Source
|  |  | Raw | Raw | Raw | Raw | Raw | Raw
Turbidity | NTU | 0.1 | 0.5 | 6 | 4 | 0.9 | 0.6 | 1.4
TDS (Calc. from Cond.) | mg/L | 1 | 25 | 59 | 82 | 89 | 43 | 56
Surfactants Content | mg/L | 0.05 | 0.05 | <0.05 | <0.05 | <0.05 | <0.05 | <0.05
Dissolved Organic Carbon | mg/L | 0.2 | 0.4 | 1.8 | 1 | <0.2 | 0.5 | 1.1
Chloride | mg/L | 0.5 | 2.9 | 2.3 | 1.8 | 2.2 | 4.6 | 4.9
Fluoride | mg/L | 0.1 | < 0.1 | <0.1 | <0.1 | 0.1 | <0.1 | <0.1
Nitrite (N) | mg/L | 0.1 | < 0.1 | <0.1 | <0.1 | 0.1 | <0.1 | <0.1
Nitrate (N) | mg/L | 0.1 | < 0.1 | 0.1 | 0.2 | 0.2 | 0.1 | 0.3
Sulphate | mg/L | 1 | < 1 | 4 | 2 | 6 | 3 | 6
Phenolics | mg/L | 0.001 | < 0.001 | <0.001 | <0.001 | <0.001 | <0.001 | <0.001
Arsenic | mg/L | 0.0001 | < 0.0001 | <0.0001 | <0.0001 | <0.005 | <0.0001 | <0.0001
Barium | mg/L | 0.001 | 0.034 | 0.004 | 0.013 | 0.013 | 0.004 | <0.001
Cadmium | mg/L | 1.4e-05 | < 0.000014 | <0.000014 | <0.000014 | <0.00002 | <0.00002 | <0.00002
Chromium | mg/L | 0.002 | < 0.002 | <0.002 | <0.002 | <0.002 | <0.002 | <0.002
Chromium (VI) | mg/L | 0.002 | < 0.002 | <0.002 | <0.002 | <0.002 | <0.002 | <0.002
Copper | mg/L | 0.002 | 0.016 | <0.002 | <0.002 | <0.002 | 0.004 | <0.002
Cyanide (Total) | mg/L | 0.005 | < 0.005 | <0.005 | <0.005 | <0.005 | <0.005 | <0.005
Iron | mg/L | 0.005 | 0.043 | 0.385 | 0.061 | 0.039 | 0.018 | 0.009
Lead | mg/L | 2e-05 | 0.00044 | 0.00018 | 0.0007 | <0.00002 | 3e-05 | <0.00002
Manganese | mg/L | 0.001 | 0.001 | 0.02 | 0.003 | 0.002 | 0.001 | 0.003
Selenium | mg/L | 0.001 | < 0.001 | <0.001 | <0.001 | <0.001 | <0.001 | <0.001
Silver | mg/L | 2e-05 | 2e-05 | <0.00002 | <0.00002 | <0.00002 | <0.00002 | <0.00002
Zinc | mg/L | 0.005 | 0.039 | <0.005 | <0.005 | <0.005 | 0.016 | <0.005
E coli | cfu/100mL | 1 | 0 | 0 | 0

## B18-21981
Certificate of Analysis | [7 empty] | REPORT No. B18-21981
Final Report
Report To: |  |  |  |  | Caduceon Environmental Laboratories
Hamlet of Grise Fiord |  |  |  |  | 2378 Holly Lane
P.O. Box 77 Grise Fiord, |  |  |  |  | Ottawa Ontario K1V 7P1
Grise Fiord NU X0X 0J0 |  |  |  |  | Tel: 613-526-0123
Attention: | SAO - |  |  |  | Fax: 613-526-1244
DATE SUBMITTED: | 2018-07-25 14:33 |  |  |  | JOB/PROJECT NO.: |  | Raw Drinking Water
DATE REPORTED: | 2018-08-10 |  |  |  | P.O. NUMBER:
SAMPLE MATRIX: | Drinking Water |  |  |  | WATERWORKS NO.:
|  |  | Client ID: |  | Primary | Secondary | Nozzle
|  |  | Sample ID: |  | B18-21981-1 | B18-21981-2 | B18-21981-3
|  |  | Date Collected: |  | 17-Jul-18 | 17-Jul-18 | 17-Jul-18
Parameter | Units | M.D.L. | Reference Method | Date/Site Analyzed
TDS (Calc. from Cond.) | mg/L | 1 | Calc. | 2018-07-30 | 23 | 63 | 21
Chloride | mg/L | 0.5 | SM4110C | 25-Jul-18/O | 2.2 | 1.4 | 3.8
Fluoride | mg/L | 0.1 | SM4110C | 25-Jul-18/O | < 0.1 | < 0.1 | < 0.1
Nitrate (N) | mg/L | 0.1 | SM4110C | 25-Jul-18/O | < 0.1 | < 0.1 | < 0.1
Nitrite (N) | mg/L | 0.1 | SM4110C | 25-Jul-18/O | < 0.1 | < 0.1 | < 0.1
Sulphate | mg/L | 1 | SM4110C | 25-Jul-18/O | 2 | 1 | 2
Cyanide (Total) | mg/L | 0.005 | SM 4500CN | 31-Jul-18/K | < 0.005 | < 0.005 | < 0.005
Arsenic | mg/L | 0.0001 | EPA 200.8 | 26-Jul-18/O | < 0.0001 | < 0.0001 | < 0.0001
Barium | mg/L | 0.001 | SM 3120 | 26-Jul-18/O | 0.001 | 0.01 | 0.037
Cadmium | mg/L | 1.5e-05 | EPA 200.8 | 26-Jul-18/O | < 0.000015 | < 0.000015 | 1.9e-05
Chromium | mg/L | 0.002 | SM 3120 | 26-Jul-18/O | < 0.002 | < 0.002 | < 0.002
Chromium (VI) | mg/L | 0.002 | MOE E3056 | 30-Jul-18/O | < 0.002 | < 0.002 | < 0.002
Copper | mg/L | 0.002 | SM 3120 | 26-Jul-18/O | 0.002 | < 0.002 | 0.014
Iron | mg/L | 0.005 | SM 3120 | 26-Jul-18/O | 0.01 | 0.034 | 0.018
Lead | mg/L | 2e-05 | EPA 200.8 | 26-Jul-18/O | < 0.00002 | < 0.00002 | 0.00044
Manganese | mg/L | 0.001 | SM 3120 | 26-Jul-18/O | < 0.001 | 0.001 | 0.001
Selenium | mg/L | 0.001 | EPA 200.8 | 26-Jul-18/O | < 0.001 | < 0.001 | < 0.001
Silver | mg/L | 0.0001 | EPA 200.8 | 26-Jul-18/O | < 0.0001 | < 0.0001 | < 0.0001
Zinc | mg/L | 0.005 | SM 3120 | 26-Jul-18/O | < 0.005 | < 0.005 | 0.048
Phenolics | mg/L | 0.001 | MOEE 3179 | 27-Jul-18/O | < 0.001 | < 0.001 | < 0.001
Dissolved Organic Carbon | mg/L | 0.2 | EPA 415.1 | 30-Jul-18/O | 0.8 | 0.4 | 0.7
Surfactants Content | mg/L | 0.05 | SM-5540-C | 08-Aug-18/O | < 0.05 | < 0.05 | < 0.05
E coli | cfu/100mL | 1 | MOE E3407 | 25-Jul-18/O | 0 | 0 | 0

## B18-22020
Certificate of Analysis | [7 empty] | REPORT No. B18-22020
Final Report
Report To: |  |  |  |  | Caduceon Environmental Laboratories
Hamlet of Grise Fiord |  |  |  |  | 2378 Holly Lane
P.O. Box 77 Grise Fiord, |  |  |  |  | Ottawa Ontario K1V 7P1
Grise Fiord NU X0X 0J0 |  |  |  |  | Tel: 613-526-0123
Attention: | SAO - |  |  |  | Fax: 613-526-1244
DATE SUBMITTED: | 2018-07-25 15:46 |  |  |  | JOB/PROJECT NO.: |  | Waste Water
DATE REPORTED: | 2018-08-01 |  |  |  | P.O. NUMBER:
SAMPLE MATRIX: | Waste Water |  |  |  | WATERWORKS NO.:
|  |  | Client ID: |  | Sample #1 | Sample #2
|  |  | Sample ID: |  | B18-22020-1 | B18-22020-2
|  |  | Date Collected: |  | 17-Jul-18 | 17-Jul-18
Parameter | Units | M.D.L. | Reference Method | Date/Site Analyzed
Hardness (as CaCO3) | mg/L | 1 | SM 3120 | 26-Jul-18/O | 64 | 64
Alkalinity(CaCO3) to pH4.5 | mg/L | 5 | SM 2320B | 27-Jul-18/O | 201 | 213
pH @25°C | pH Units |  | SM 4500H | 27-Jul-18/O | 7.46 | 7.38
Conductivity @25°C | µmho/cm | 1 | SM 2510B | 27-Jul-18/O | 613 | 616
Total Suspended Solids | mg/L | 3 | SM2540D | 27-Jul-18/K | 40 | 30
Chloride | mg/L | 0.5 | SM4110C | 30-Jul-18/O | 34.1 | 34.3
Nitrite (N) | mg/L | 0.1 | SM4110C | 30-Jul-18/O | < 0.1 | < 0.1
Nitrate (N) | mg/L | 0.1 | SM4110C | 30-Jul-18/O | < 0.1 | < 0.1
Sulphate | mg/L | 1 | SM4110C | 30-Jul-18/O | 4 | 5
Aluminum | mg/L | 0.01 | SM 3120 | 26-Jul-18/O | 0.1 | 0.09
Arsenic | mg/L | 0.0001 | EPA 200.8 | 26-Jul-18/O | < 0.0005 | < 0.0005
Cadmium | mg/L | 0.005 | SM 3120 | 26-Jul-18/O | < 0.005 | < 0.005
Calcium | mg/L | 0.02 | SM 3120 | 26-Jul-18/O | 17.6 | 17.4
Chromium | mg/L | 0.002 | SM 3120 | 26-Jul-18/O | < 0.002 | 0.002
Cobalt | mg/L | 0.005 | SM 3120 | 26-Jul-18/O | 0.01 | 0.017
Copper | mg/L | 0.002 | SM 3120 | 26-Jul-18/O | 0.058 | 0.058
Iron | mg/L | 0.005 | SM 3120 | 26-Jul-18/O | 0.321 | 0.279
Lead | mg/L | 0.02 | SM 3120 | 26-Jul-18/O | < 0.02 | < 0.02
Magnesium | mg/L | 0.02 | SM 3120 | 26-Jul-18/O | 4.82 | 4.88
Manganese | mg/L | 0.001 | SM 3120 | 26-Jul-18/O | 0.031 | 0.029
Mercury | mg/L | 2e-05 | SM 3112 B | 30-Jul-18/O | 2e-05 | 2e-05
Nickel | mg/L | 0.01 | SM 3120 | 26-Jul-18/O | < 0.01 | < 0.01
Potassium | mg/L | 0.1 | SM 3120 | 26-Jul-18/O | 16.4 | 16.8
Sodium | mg/L | 0.2 | SM 3120 | 26-Jul-18/O | 39.7 | 41.4
Zinc | mg/L | 0.005 | SM 3120 | 26-Jul-18/O | 0.073 | 0.073
Ammonia (N)-Total | mg/L | 0.01 | SM4500-NH3-H | 30-Jul-18/K | 32 | 31.8
Phenolics | mg/L | 0.001 | MOEE 3179 | 30-Jul-18/K | 0.034 | 0.034
BOD | mg/L | 3 | SM 5210B | 26-Jul-18/O | 143 | 156
Total Organic Carbon | mg/L | 0.2 | EPA 415.1 | 30-Jul-18/O | 63.1 | 71.4
Oil & Grease-Total | mg/L | 1 | SM 5520 | 30-Jul-18/K | 6.4 | 7.6
Fecal Coliform | cfu/100mL | 1 | MOE E3371 | 25-Jul-18/O | 12000 | 11000