## Overall - ONLY NWB Maximums
Test Group | Frequency | Flow - F | General - G | [11 empty] | Metals -M | [14 empty] | Sewage - S |  |  | Hydrocarbon - H
Parameter |  | Volume (m3) | pH | Conductivity (uS/cm) | Temperature (oC ) | Total Suspended Solids (TSS) (mg/L) | Oil and Grease (mg/L) | Nitrate-Nitrite (mg/L) | Ammonia Nitrogen (mg/L) | Sulphate (mg/L) | Total Hardness (mg/L) | Total Alkalinity (mg/L) | Total Phenols (mg/L) | Total Organic Carbon - TOC (mg/L) | Al (mg/L) | Ar (mg/L) | As (mg/L) | Ca (mg/L) | Cd (mg/L) | Cr (mg/L) | Cu (mg/L) | Fe (mg/L) | Hg (mg/L) | K (mg/L) | Mg (mg/L) | Na (mg/L) | Ni (mg/L) | Pb (mg/L) | Zn (mg/L) | Fecal Coliform (CFU/100 mL) | Biochemical Oxygen Demand (mg/L) | Chloride (mg/L) | TPH (Total Petroleum Hydrocarbons) | PAH (Polycyclic Aromatic Hydrocarbons) | BTEX
[35 empty] | Benzene (mg/L) | Toluene (mg/L) | Ethylbenzene (mg/L) | Xylene (mg/L)
ALT-1 | Daily | 875 per day
ALT-2 | Bi-Weekly
ALT-3 | Bi-Weekly |  | 6 to 9 |  |  | 70 | 5 + no visible sheen | [23 empty] | 80
ALT-4 | When discharge occurs
ALT-5 | When discharge occurs
ALT-6 | When discharge occurs
ALT-7 | When discharge occurs
ALT-8 | When discharge occurs | [5 empty] | 15 + no visible sheen | [5 empty] | 0.02 | [14 empty] | 0.001 | [6 empty] | 0.37 | 0.002 | 0.09
ALT-9 | When discharge occurs | [5 empty] | 15 + no visible sheen | [5 empty] | 0.02 | [14 empty] | 0.001 | [6 empty] | 0.37 | 0.002 | 0.09
ALT-10 | When discharge occurs | [5 empty] | 15 + no visible sheen | [5 empty] | 0.02 | [14 empty] | 0.001 | [6 empty] | 0.37 | 0.002 | 0.09
ALT-11 | When discharge occurs | [5 empty] | 15 + no visible sheen | [5 empty] | 0.02 | [14 empty] | 0.001 | [6 empty] | 0.37 | 0.002 | 0.09
ALT-12 | When discharge occurs | [5 empty] | 15 + no visible sheen | [5 empty] | 0.02 | [14 empty] | 0.001 | [6 empty] | 0.37 | 0.002 | 0.09
ALT-13 | Bi-Weekly |  | 6 to 9 |  |  | 70 | 5 + no visble sheen | [23 empty] | 80

## CCME + NWB Maximums
Test Group | Frequency | Flow - F | General - G | [11 empty] | Metals -M | [14 empty] | Sewage - S |  |  | Hydrocarbon - H
Parameter |  | Volume (m3) | pH | Conductivity (uS/cm) | Temperature (oC ) | Total Suspended Solids (TSS) (mg/L) | Oil and Grease (mg/L) | Nitrate-Nitrite (mg/L) | Ammonia Nitrogen (mg/L) | Sulphate (mg/L) | Total Hardness (mg/L) | Total Alkalinity (mg/L) | Total Phenols (mg/L) | Total Organic Carbon - TOC (mg/L) | Al (mg/L) | Ar (mg/L) | As (mg/L) | Ca (mg/L) | Cd (mg/L) | Cr (mg/L) | Cu (mg/L) | Fe (mg/L) | Hg (mg/L) | K (mg/L) | Mg (mg/L) | Na (mg/L) | Ni (mg/L) | Pb (mg/L) | Zn (mg/L) | Fecal Coliform (CFU/100 mL) | Biochemical Oxygen Demand (mg/L) | Chloride (mg/L) | TPH (Total Petroleum Hydrocarbons) | PAH (Polycyclic Aromatic Hydrocarbons) | BTEX
[35 empty] | Benzene (mg/L) | Toluene (mg/L) | Ethylbenzene (mg/L) | Xylene (mg/L)
ALT-1 Water Supply at Raw Water Intake (or Pumphouse) | Daily | 875 per day
ALT-2 Discharge Point at the Sewage Outfall (prior to treatment) | Bi-Weekly
ALT-3 Final Discharge Point of the Wastewater Treatment Facilities at weir box or similar structure, prior to entry into Parr Inlet | Bi-Weekly |  | 6 to 9 |  |  | 70 | 5 + no visible sheen | [23 empty] | 80
ALT-4 Runoff and leachate from the Main Station Landfill | When discharge occurs
ALT-5 Runoff and leachate from the Battery Dump | When discharge occurs
ALT-6 Runoff and leachate from the Millionaire’s Dump | When discharge occurs
ALT-7 Runoff and leachate from Dump 3 | When discharge occurs
ALT-8 Discharge from Lower/Airfield Fuel Tank Farm secondary containment | When discharge occurs | [5 empty] | 15 + no visible sheen | [5 empty] | 0.02 | [14 empty] | 0.001 | [6 empty] | 0.37 | 0.002 | 0.09
ALT-9 Discharge from Upper Fuel Tank Farm secondary containment | When discharge occurs | [5 empty] | 16 + no visible sheen | [5 empty] | 0.02 | [14 empty] | 0.001 | [6 empty] | 0.37 | 0.002 | 0.09
ALT-10 Discharge from Day Fuel Tank Farm secondary containment | When discharge occurs | [5 empty] | 17 + no visible sheen | [5 empty] | 0.02 | [14 empty] | 0.001 | [6 empty] | 0.37 | 0.002 | 0.09
ALT-11 Discharge from the Airfield Landfarm | When discharge occurs | [5 empty] | 18 + no visible sheen | [5 empty] | 0.02 | [14 empty] | 0.001 | [6 empty] | 0.37 | 0.002 | 0.09
ALT-12 Discharge from the Day Fuel Tank Landfarm | When discharge occurs | [5 empty] | 19 + no visible sheen | [5 empty] | 0.02 | [14 empty] | 0.001 | [6 empty] | 0.37 | 0.002 | 0.09
ALT-13 Final Discharge Point from the Wastewater Treatment Plant | Bi-Weekly |  | 6 to 9 |  |  | 70 | 5 + no visble sheen | [23 empty] | 80

## ALT - 1 Water Withdrawals
2025
ALT -1 | Water withdrawl (m3/day)
| January | February | March | April | May | June | July | August | September | October | November | December
1 | 313 | 272 | 353 | 276 | 280 | 265 | 293 | 205 | 249 | 282 | 258 | 206
2 | 197 | 315 | 302 | 251 | 272 | 235 | 250 | 306 | 315 | 174 | 229 | 219
3 | 258 | 358 | 223 | 338 | 297 | 302 | 336 | 271 | 359 | 212 | 216 | 282
4 | 289 | 277 | 266 | 242 | 260 | 291 | 259 | 269 | 215 | 258 | 224 | 199
5 | 277 | 265 | 263 | 298 | 251 | 298 | 285 | 275 | 346 | 219 | 205 | 227
6 | 235 | 252 | 350 | 243 | 287 | 314 | 277 | 260 | 269 | 185 | 226 | 221
7 | 240 | 268 | 203 | 243 | 278 | 283 | 327 | 0 | 273 | 226 | 224 | 252
8 | 249 | 297 | 302 | 275 | 272 | 276 | 286 | 334 | 244 | 227 | 261 | 235
9 | 260 | 274 | 265 | 294 | 275 | 273 | 285 | 334 | 313 | 187 | 231 | 226
10 | 269 | 334 | 216 | 259 | 227 | 274 | 277 | 197 | 256 | 241 | 187 | 200
11 | 282 | 260 | 256 | 263 | 340 | 333 | 331 | 342 | 284 | 252 | 279 | 237
12 | 246 | 269 | 273 | 307 | 247 | 223 | 263 | 268 | 273 | 193 | 184 | 167
13 | 220 | 257 | 266 | 261 | 294 | 282 | 271 | 253 | 227 | 177 | 231 | 261
14 | 275 | 291 | 258 | 258 | 214 | 328 | 310 | 269 | 255 | 210 | 214 | 241
15 | 240 | 280 | 301 | 245 | 310 | 245 | 214 | 294 | 270 | 202 | 233 | 172
16 | 134 | 265 | 284 | 280 | 316 | 275 | 281 | 475 | 328 | 202 | 263 | 218
17 | 157 | 255 | 229 | 275 | 307 | 219 | 279 | 152 | 158 | 220 | 190 | 193
18 | 255 | 248 | 278 | 301 | 289 | 246 | 283 | 235 | 349 | 195 | 204 | 244
19 | 253 | 286 | 274 | 260 | 288 | 353 | 300 | 293 | 252 | 227 | 245 | 173
20 | 262 | 275 | 291 | 272 | 255 | 311 | 272 | 270 | 260 | 215 | 209 | 221
21 | 259 | 267 | 278 | 265 | 344 | 347 | 259 | 273 | 358 | 228 | 223 | 213
22 | 259 | 271 | 299 | 253 | 246 | 267 | 281 | 275 | 128 | 277 | 260 | 236
23 | 262 | 272 | 249 | 245 | 287 | 259 | 290 | 402 | 354 | 225 | 206 | 201
24 | 238 | 250 | 246 | 276 | 317 | 254 | 287 | 276 | 245 | 207 | 214 | 200
25 | 278 | 275 | 277 | 267 | 294 | 283 | 301 | 216 | 249 | 195 | 250 | 209
26 | 277 | 276 | 277 | 285 | 311 | 271 | 294 | 271 | 204 | 261 | 174 | 218
27 | 252 | 255 | 292 | 257 | 229 | 293 | 269 | 273 | 351 | 166 | 244 | 216
28 | 487 | 269 | 269 | 262 | 298 | 379 | 283 | 396 | 402 | 208 | 226 | 214
29 | 251 |  | 307 | 311 | 286 | 304 | 263 | 247 | 204 | 233 | 262 | 205
30 | 239 |  | 305 | 233 | 275 | 244 | 281 | 385 | 290 | 228 | 218 | 224
31 | Water withdrawl (m3/day) January: 279; Water withdrawl (m3/day) March: 206; Water withdrawl (m3/day) May: 327; Water withdrawl (m3/day) July: 375; Water withdrawl (m3/day) August: 244; Water withdrawl (m3/day) October: 191; Water withdrawl (m3/day) December: 224 | Total (m3): | averge daily (m3)
sum (m3): | 7992 | 7733 | 8458 | 8095 | 8773 | 8527 | 8862 | 8560 | 8280 | 6723 | 6790 | 6754 | 95547 | 261.7726
Note: if amount greater than 875 it will highlight itself red
ex | Water withdrawl (m3/day) January: 900

## ALT 2 - 13 Results
Test Group | Frequency | Date Samples Taken | Flow - F | General - G | [11 empty] | Metals -M | [14 empty] | Sewage - S |  |  | Hydrocarbon - H
Parameter |  |  | Volume (m3) | pH | Conductivity (uS/cm) | Temperature (oC ) | Total Suspended Solids (TSS) (mg/L) | Oil and Grease (mg/L) | Nitrate-Nitrite (mg/L) | Ammonia Nitrogen (mg/L) | Sulphate (mg/L) | Total Hardness (mg/L) | Total Alkalinity (mg/L) | Total Phenols (mg/L) | Total Organic Carbon - TOC (mg/L) | Al (mg/L) | Ar (mg/L) | As (mg/L) | Ca (mg/L) | Cd (mg/L) | Cr (mg/L) | Cu (mg/L) | Fe (mg/L) | Hg (mg/L) | K (mg/L) | Mg (mg/L) | Na (mg/L) | Ni (mg/L) | Pb (ug/L) | Zn (mg/L) | Fecal Coliform (CFU/100 mL) | Biochemical Oxygen Demand (mg/L) | Chloride (mg/L) | TPH (Total Petroleum Hydrocarbons) | PAH (Polycyclic Aromatic Hydrocarbons) | BTEX
[34 empty] | ug/L | ug/L | Benzene (ug/L) | Toluene (ug/L) | Ethylbenzene (ug/L) | Xylene (ug/L)
ALT-2 | Bi-Weekly
|  | 2025-06-30 |  | 7.78 | 483 |  | 41.1 | 12 | <0.01 | 10.1 | 8.67 | 138 | 182 | 0.008 | 49.4 | 0.0811 |  | 0.0046 | 43.8 | 0.00212 | 0.00071 | 0.18 | 0.185 | 6.3e-06 | 5.82 | 6.97 | 16.3 | 0.0017 | 0.947 | 0.446 | NR | 53.2 | 26.2
|  | 2025-07-01 |  | 7.16 | 414 |  | 236 | 71 | <0.01 | 11.7 | 10.4 | 135 | 145 | 0.0094 | 40.4 | 0.115 |  | 0.00049 | 43.1 | 0.000147 | 0.00081 | 0.252 | 0.283 | <0.0000050 | 7.68 | 6.76 | 17.1 | 0.00158 | 1.36 | 0.0469 | NR | 129 | 25.3
|  | 2025-08-30 |  | 7.9 | 458 |  | 38.2 | 23 | 0.032 | 3.62 | 6.95 | 108 | 161 | 0.0036 | 48 | 0.108 |  | 0.0004 | 33.9 | 4.84e-05 | 0.00055 | 0.0999 | 0.162 | 5.5e-06 | 4.01 | 5.61 | 29.8 | 0.00115 | 0.878 | 0.0342 | NR | 30 | 31.6
|  | 2025-09-03 |  | 7.79 | 460 |  | 33.85 | <5.0 | <0.01 | 6.76 | 8.06 | 106 | 176 | 0.0073 | 33.2 | 0.0288 |  | 0.00031 | 33.6 | 2.06e-05 | <0.00050 | 0.0882 | 0.062 | <0.0000050 | 7.03 | 5.36 | 16.6 | 0.0165 | 0.562 | 0.0165 | NR | 44.3 | 21.9
ALT-3 | Bi-Weekly |  |  | 6 to 9 |  |  | 70 | 5 + no visible sheen | [23 empty] | 80
|  | JUN | UNACCESSIBLE-FROZEN
|  | JUL | UACCESSIBLE- FROZEN
|  | 2025-08-30 |  | 7.8 | 404 |  | 111 | 12.6 | <0.01 | 8.39 | 6.02 | 141 | 158 | 0.0045 | 29.8 | 0.883 |  | 0.00264 | 44.4 | 4.71e-05 | 0.00221 | 0.0809 | 2.37 | 5.8e-06 | 4.24 | 7.4 | 15.8 | 0.00607 | 1.97 | 0.0248 | NR | 30.1 | 19.5
|  | 2025-09-03 |  | 7.87 | 424 |  | 70.4 | 23.4 | 0.044 | 6.6 | 6.84 | 146 | 156 | 0.0042 | 23.4 | 0.688 |  | 0.00324 | 45.8 | 4.74e-05 | 0.00164 | 0.0838 | 2.02 | <0.0000050 | 5.04 | 7.67 | 21.6 | 0.025 | 1.66 | 0.025 | NR | 10.9 | 26.6
ALT-4 | When discharge occurs
|  | 2025-06-30 |  | 8.03 | 212 | 1.6 | 48.1 | <5.0 | 0.229 | <0.0050 | 16.2 | 85.8 | 65.5 | 0.0036 | 1.67 | 0.686 |  | 0.00289 | 26 | 3.22e-05 | 0.00161 | 0.0057 | 1.33 | <0.0000050 | 2.99 | 5.08 | 11 | 0.00472 | 1.8 | 0.0105
|  | 2025-07-01 |  | 7.99 | 213 | 1.7 | 28.1 | <5.0 | 0.22 | <0.0050 | 15.7 | 79.9 | 64.6 | 0.0039 | 2.11 | 0.434 |  | 0.0022 | 24.2 | 1.62e-05 | 0.0011 | 0.00311 | 0.738 | <0.0000050 | 3.04 | 4.72 | 11.3 | 0.0032 | 1.17 | 0.0065
|  | Aug | FROZEN
|  | Sep | FROZEN
ALT-5 | When discharge occurs
|  | 2025-06-30 |  | 8.13 | 221 | 5.1 | 8.5 | <5.0 | 0.119 | 0.0078 | 26.4 | 34.1 | 67.3 | 0.0112 | 0.7 | 0.424 |  | 0.023 | 10.8 | <0.0000050 | 0.0008 | 0.00256 | 0.648 | <0.0000050 | 3.59 | 1.74 | 31.8 | 0.00452 | 1.25 | 0.0036
|  | 2025-07-01 |  | 8.13 | 211 | 5 | 22.5 | <5.0 | 0.11 | 0.0074 | 25.1 | 31.7 | 69.3 | 0.002 | 0.88 | 0.474 |  | 0.0232 | 10.2 | 6.1e-06 | 0.00093 | 0.00256 | 0.714 | <0.0000050 | 3.6 | 1.52 | 30.9 | 0.00523 | 1.22 | 0.004
|  | Aug | DRY
|  | Sep | DRY
ALT-6 | When discharge occurs
|  | 2025-06-30 |  | 7.98 | 175 | 10.7 | 160 | <5.0 | 0.073 | 0.0142 | 34 | 115 | 38.4 | 0.005 | 1.66 | 1.98 |  | 0.00187 | 31.9 | 1.7e-05 | 0.00388 | 0.00468 | 3.61 | <0.0000050 | 1.12 | 8.6 | 4.48 | 0.00717 | 2.57 | 0.0104
|  | 2025-07-01 |  | 8.1 | 156 | 10.5 | 210 | <5.0 | 0.117 | 0.0062 | 12.7 | 120 | 49.8 | 0.0045 | 3.49 | 3.37 |  | 0.00446 | 33.3 | 3.69e-05 | 0.00653 | 0.00854 | 6.46 | 6e-06 | 4.14 | 8.99 | 17.3 | 0.0121 | 4.23 | 0.0202
|  | Aug | DRY
|  | Sep | DRY
ALT-7 | When discharge occurs
|  | 2025-06-30 |  | 8.06 | 266 | 8.1 | 135 | <5.0 | 0.1 | 0.0058 | 43.1 | 81.7 | 54.2 | 0.0021 | 2.03 | 1.51 |  | 0.00209 | 22 | 1.64e-05 | 0.00305 | 0.00409 | 2.56 | <0.0000050 | 4.5 | 6.5 | 19.3 | 0.0055 | 1.68 | 0.0102
|  | 2025-07-01 |  | 8 | 172 | 8.1 | 195 | <5.0 | 0.066 | 0.0151 | 32.9 | 105 | 37.5 |  | 1.74 | 2.78 |  | 0.0025 | 31.5 | 2.3e-05 | 0.00527 | 0.00615 | 5.09 | <0.0000050 | 1.1 | 6.45 | 2.09 | 0.00979 | 3.46 | 0.0143
|  | Aug | DRY
|  | Sep | DRY
ALT-8 | When discharge occurs | [6 empty] | 15 + no visible sheen | [5 empty] | 0.02 | [14 empty] | 1 | [6 empty] | 370 | 2 | 90
|  | 2025-06-30 |  | 8 |  |  | <3.0 | <5.0 | [5 empty] | 0.0055 | [14 empty] | 2.67 |  |  |  |  | <370 | <0.40 | <0.50 | <0.50 | <0.50 | <0.40
|  | 2025-07-01 |  | 8.01 |  |  | <3.0 | <5.0 | [5 empty] | 0.0019 | [14 empty] | 2.76 |  |  |  |  | <370 | <0.40 | <0.50 | <0.50 | <0.50 | <0.40
ALT-8.1 | When discharge occurs | [6 empty] | 15 + no visible sheen | [5 empty] | 0.02 | [14 empty] | 1 | [6 empty] | 370 | 2 | 90
|  | 2025-06-30 |  | 8.12 |  |  | 3.5 | <5.0 | [5 empty] | 0.0013 | [14 empty] | 0.289 |  |  |  |  | <370 | <0.40 | <0.50 | <0.50 | <0.50 | <0.40
|  | 2025-07-01 |  | 8.12 |  |  | <3.0 | <5.0 | [5 empty] | 0.0062 | [14 empty] | 0.317 |  |  |  |  | <370 | <0.40 | <0.50 | <0.50 | <0.50 | <0.40
ALT-9 | When discharge occurs | [6 empty] | 15 + no visible sheen | [5 empty] | 0.02 | [14 empty] | 1 | [6 empty] | 370 | 2 | 90
|  | 2025-06-30 |  | 8.08 |  |  | <3.0 | <5.0 | [5 empty] | 0.0036 | [14 empty] | 0.174 |  |  |  |  | <370 | <0.40 | <0.50 | <0.50 | <0.50 | <0.40
|  | 2025-07-01 |  | 8.05 |  |  | <3.0 | <5.0 | [5 empty] | 0.0034 | [14 empty] | 0.194 |  |  |  |  | <370 | <0.40 | <0.50 | <0.50 | <0.50 | <0.40
ALT-10 | When discharge occurs | [6 empty] | 15 + no visible sheen | [5 empty] | 0.02 | [14 empty] | 1 | [6 empty] | 370 | 2 | 90
|  | 2025-06-30 | DRY
ALT-11 | When discharge occurs | [6 empty] | 15 + no visible sheen | [5 empty] | 0.02 | [14 empty] | 1 | [6 empty] | 370 | 2 | 90
|  | 2025-06-30 | DRY
ALT-12 | When discharge occurs | [6 empty] | 15 + no visible sheen | [5 empty] | 0.02 | [14 empty] | 1 | [6 empty] | 370 | 2 | 90
|  | 2025-06-30 | DRY
ALT-13 | Bi-Weekly |  |  | 6 to 9 |  |  | 70 | 5 + no visble sheen | [23 empty] | 80
|  | N/A | N/A