[image: image1.png]NASITTUQ



Nunavut Water Board Annual Report 2007

 Submitted by Nasittuq Corporation [image: image2.png]





[image: image5.png]66.614167, 61.619444

| _tap | Satolite | Terain |
[ srow oer]

v sho

:

2008 Google - Inagery 2008 DigitalGlobe, Map data G2008 NAYTEG™ - T

2000
S00m :\# =




ANNUAL REPORT 2007
Submitted to: 

Nunavut Water Board 

For 

Licence:
NWB6DYE0409 - Type “B”

                  DYE-M, Cape Dyer, NU

Submitted by:  Nasittuq Corporation

31 March 2008
This annual report is submitted to the Nunavut Water Board (NWB) as stipulated in Para. 1, Part B, General Conditions of the following licence:

Licence: NWB6DYE0409 Type “B”

NUNAVUT WATER LICENCE:  NWB6DYE0409 Type “B”

North Warning System Long Range Radar – DYE-M, Cape Dyer, Nunavut
The annual operation and maintenance (O&M) activities at Cape Dyer during the reporting period included the quarterly preventive/corrective maintenance, in-house regulatory compliance audits and inspections, routine infrastructure maintenance in preparation for the summer RAMP-UP activities, and fuel resupply.  Specific summer projects were Edwards Fire Alarm Panel Replacement, Water Tank Replacement, B-Train Accommodation Upgrade and DLCU Construction.
Water Use 

The site reverted to the annual transitory manned status in early May and ramped down in late October, totaling 178 days of continuous site occupancy.  The calculated total water usage for the site is 320.4 cubic meters.  This is based on 150 litres per person per day, with an average daily occupancy rate of 12 persons.  This gives an average daily usage of 1.8 cubic meters, below the 10 cubic meters daily allowed by the license.  Note that a water meter has since been installed at the site, and for the 2009 report, we will be able to report actual usage.

Hazardous Waste Disposal
The waste management was consistent with the Nasittuq Environmental Protection Plan, meeting the terms and conditions stipulated in the NWB water licence.

The following items were retrograded to Quebec for disposal in 2007.
Disposal facility: Recyclex, 8381, Place Marien, Montreal-EST Quebec. H1B 5W6
Summary of Waste Retrograde in 2007
	DYE-M
	Glycol
	1 drum

	DYE-M
	Waste Fuel
	1 drum

	DYE-M
	Waste fuel mixture
	1 drum

	DYE-M
	Waste oil filters
	1 drum

	DYE-M
	Waste fuel filters
	1 drum

	DYE-M
	Waste paint
	1 drum

	DYE-M
	Waste batteries, wet, lead acid
	3 crates

	DYE-M
	Waste batteries, non-spill
	1 crate

	DYE-M
	Waste Oil
	1 crate 25 x 5 gal pails

	DYE-M
	Waste Oil
	17 drums


Non Hazardous Solid Waste Disposal

All domestic solid waste was disposed of by burning in a burn bin and buried at a designated on-site landfill.

Refer to Annex A for designated landfill location, with GPS coordinates at DYE-M.

Sewage Discharge

Refer to Annex B for sewage outfall location, with GPS coordinates at DYE-M.

Monitoring Program

Refer to Annex C for sewage analysis for DYE-M.

Product Spills

Two spills occurred during this reporting period.

	Date
	Product
	Quantity
	Cause 
	Locality

	02 Jun 2007
	Jet A-1
	Residue
	Cracked flange on empty tank
	DYE-M Airstrip

	26 July 2007
	Jet A-1
	3 litres
	Bung on a Drum was loose
	DYE-M near Burn bin


Revisions to the ERP 

No revisions have been effected during this reporting period.

Progressive reclamation work undertaken 

There was a significant reclamation effort at DYE-MAIN in 2007.  However, this work was implemented by Defence Construction Canada (DCC) as part of the larger DEW Line Clean-Up (DLCU) project.  As such, this work was not under the care custody or control of Nasittuq Corporation.

Annex A
Designated landfill location, with GPS coordinates at DYE-M.
DYE-M

[image: image3.png]100m b -
\ﬁum %‘ " @2007 Google - Imagery ©2007 DigitalGlobaTerraMetrics, Map data ©2007 NAVTEQ™ - Terms of Use.





Annex B
Sewage outfall location, with GPS coordinates at DYE-M
[image: image4.png][_vap_[ Sateiite | Terran ]

& %
<
' -
66.664239, -61.354594 .
211
s
: Get directions
-
P

som <
00t ©2007 Google - Imagery @2007 DigitalGlobe, TerraMetrics, Map data ©2007 NAYTEQ™ - Terms of Use.



DYE-M
Annex C
Sewage analysis for DYE-M.
	Client:   Nasittuq Corp. (Ottawa)
	
	
	
	
	
	
	Report Number:  2803213

	100-170 Laurier Ave. West Ottawa, ON 

K1P 5V5
	
	
	
	
	
	
	Date:                     2008-02-25

	               
	
	
	
	
	
	
	Date Submitted:  2008-02-13

	Attention:     Mr. Sam Chang
	
	
	
	
	
	
	Project:
	

	
	
	
	
	
	
	
	
	

	
	
	
	
	
	
	
	P.O. Number:
	

	Chain of Custody Number:   72169
	 
	 
	 
	 
	 
	 
	Matrix:
	 Sewage

	 
	 
	LAB ID:  
	604480
	604481
	 
	 
	 
	GUIDELINE

	 
	
	Sample Date:  
	2008-01-25
	2008-01-25
	 
	 
	 
	 

	 
	
	Sample ID:  
	DYE-M
	BAF-3
	 
	 
	 
	

	PARAMETER
	UNITS
	MRL
	 
	 
	 
	 
	 
	TYPE
	LIMIT
	UNITS

	Biochemical Oxygen Demand
	mg/L
	1
	647
	3860
	 
	 
	 
	 
	 
	 

	Conductivity
	uS/cm
	5
	1130
	523
	 
	 
	 
	 
	 
	 

	N-NH3 (Ammonia)
	mg/L
	2.0
	94.4
	19.8
	 
	 
	 
	 
	 
	 

	NO2 + NO3 as N
	mg/L
	0.10
	<0.10
	<0.10
	 
	 
	 
	 
	 
	 

	pH
	 
	 
	6.61
	5.32
	 
	 
	 
	 
	 
	 

	Phenols
	mg/L
	0.001
	0.385
	0.038
	 
	 
	 
	 
	 
	 

	Sulphate
	mg/L
	1
	1
	11
	 
	 
	 
	 
	 
	 

	Total Suspended Solids
	mg/L
	2
	466
	876
	 
	 
	 
	 
	 
	 

	Calcium
	mg/L
	1
	32
	8
	 
	 
	 
	 
	 
	 

	Magnesium
	mg/L
	1
	5
	2
	 
	 
	 
	 
	 
	 

	Potassium
	mg/L
	1
	23
	50
	 
	 
	 
	 
	 
	 

	Sodium
	mg/L
	2
	64
	43
	 
	 
	 
	 
	 
	 

	Arsenic
	mg/L
	0.05
	0.06
	<0.05
	 
	 
	 
	 
	 
	 

	Cadmium
	mg/L
	0.01
	<0.01
	<0.01
	 
	 
	 
	 
	 
	 

	Chromium
	mg/L
	0.02
	0.06
	<0.02
	 
	 
	 
	 
	 
	 

	Copper
	mg/L
	0.01
	1.86
	1.92
	 
	 
	 
	 
	 
	 

	Iron
	mg/L
	0.1
	4.4
	2.3
	 
	 
	 
	 
	 
	 

	Lead
	mg/L
	0.01
	0.08
	0.02
	 
	 
	 
	 
	 
	 

	Mercury
	mg/L
	0.05
	<0.05
	<0.05
	 
	 
	 
	 
	 
	 

	Nickel
	mg/L
	0.01
	0.08
	0.02
	 
	 
	 
	 
	 
	 

	Zinc
	mg/L
	0.05
	0.56
	0.88
	 
	 
	 
	 
	 
	 

	MRL = Method Reporting Limit   INC = Incomplete   AO = Aesthetic Objective   OG = Operational Guideline   MAC = Maximum Allowable Concentration   IMAC = Interim Maximum Allowable Concentration                

	Comment:   Metals analysis performed on aqua-regia digest of sample material.

	
	APPROVAL:
	Lorna Wilson

	
	
	Agriculture Lab Supervisor


PAGE  
1

