[image: image3.jpg]




QA/QC Plan for Sampling from SHE-2

(Final Discharge Point from Sewage Disposal Facility) at CAM-3
Licensee:
Department of National Defence,


Government of Canada

Licence:
3BC-SHE0919 Type “B”
Location:
CAM-3 North Warning System Site,

Shepherd Bay, Kitikmeot Region, Nunavut
Plan submitted by:  Nasittuq Corporation
Date:

26 January 2010

Objective
This QA/QC plan applies to CAM-3’s Monitoring Station Number SHE-2, the final discharge point from the Sewage Disposal Facility.  It has been prepared to ensure that sampling, sample preservation, and analyses are done in accordance with methods in the current edition of the Standard Methods for the Examination of Water and Wastewater as required by the Nunavut Water Board Water Licence 3BC-SHE0919 Type “B”.
Review

This plan shall be reviewed annually by Nasittuq’s Environmental Services and will be updated as required.  Updated plans will be submitted to the NWB with an approval letter from a laboratory accredited to ISO/IEC Standard 17025.
Feedback
Feedback such as comments, complaints, and suggestions for improvements are to be submitted to:  Nasittuq Corp., 100-170 Laurier Ave. W., Ottawa, ON, K1P 5V5, Attention: Supervisor, Environmental Services.

Approval

This plan has been reviewed and accepted.

Original signed by Barb Thomson


26 Jan 2010
_________________________________

________________
Supervisor, Environmental Services


Date (dd/mm/yy)

Nasittuq Corp.
Background
Effluent from the Sewage Disposal Facility is discharged from a pipe to the designated outfall area.

Samples are taken of the effluent as it flows out of the pipe.  This sampling point is Monitoring Station Number SHE-2, the final discharge point from the Sewage Disposal Facility.  The liquid is adequately represented by single grab samples.
Equipment
The Sewage Testing Kit is a cooler which contains:
- a Chain of Custody form which includes an area for the sample analysis request;

- cold packs; and 
- sample bottles
provided by Exova Accutest Laboratories.  The sample bottles are listed in the table below.  The sample bottles are clean and free of contaminants.

Table 1.  Sample bottle requirements
	Bottle
	Parameters
	Sampling
	Storage Instructions

	2 x 500 ml wide-mouth plastic chem. bottles (no preservative)
	General chemistry (pH, BOD, TSS)
	Grab
	Keep cool.  Return to the laboratory within 7 days of sampling.

	1 liter amber glass (no preservative)
	Oil & Grease (total, mineral, and non-mineral), Visible sheen.
	Grab
	Keep cool.  Return to the laboratory within 7 days of sampling.

	300 ml plastic bacteria bottle with sodium thiosulphate preservative
	Faecal coliforms
	No rinsing.  Be careful not to touch open top of sterile bottle.
	Keep cool.  Arrange shipping so that laboratory receives sample within 24 hours (48 hours max) from the time of sampling.


Personal Protective Equipment (PPE)
Eye protection (safety glasses or goggles) and disposable gloves are to be worn.
Sample Collection
1. Co-ordinate taking the samples with the air cargo flight schedule to minimize sample storage time.
2. The day before sampling, get the cold packs from the sewage testing kit and place in freezer overnight.
3. The day of sampling, gather these items:
a. eye protection (safety glasses or goggles);
b. disposable gloves; 

c. Sewage Testing Kit from Logistics;
d. plastic bag (garbage bag is OK); and
e. permanent marker.
4. Go to SHE-2.
5. Put on PPE.  Remove caps from bottles.
6. Fill all bottles in kit leaving a little headspace at the top.
Note 1: Don't rinse the bottles before collecting the sample.

Note 2: Don’t touch the open top of the 300 ml sterile bottle (the smallest bottle).
7. Cap bottles.

8. With permanent marker, mark each bottle with site, unique sample #, time, and date.
9. Put bottles in garbage bag and place in cooler.  Add cold packs.

10. Complete Chain of Custody form.  See attached example.  Keep the pink sampler copy.  Place the remaining copies in the cooler.
11. Seal cooler with packing tape and air freight as soon as possible to: Exova Accutest Laboratories, 146 Colonnade Rd, Unit 8, Nepean, ON, Tel 613-727-5692.  

If any delay, keep samples cool (4 degrees C.).

Analyses
Exova Accutest Laboratories is accredited to ISO/IEC Standard 17025.  Exova has an established QA/QC program for the analyses required under this water licence (pH, Oil and Grease, Biological Oxygen Demand (BOD5), Total Suspended Solids (TSS), and Faecal Coliforms).
Results

Results are sent to Nasittuq’s Supervisor, Environmental Services.

[image: image1.jpg]200040

YT sbeg

T A O O R S5 SRt e o s SSBR S 8 KT ST
s Uy y Ut S 1 U400 U 1008

IS ‘i1 ) e P v Sewetpr

e g poneoons

(e g pamcany vow,

awouniey

o meq

s sousrisamy

ousyoeq

5

oiraasa -

P e SO IO ING 3 It s IG5 ST 7 R o e St T VAR i PSS SST S SE

NG TS 1 Ao 121304 1 LB oL« . CORRITSN0 03 FNAMEN = AN S W = M SRS e kL o S5 s SARS.

T
= Z i PR s S
7 SV r Y . < =5 T
Pl " n % w5 Tras]
SreTe T -
3y T B2 IEREs s |gleslz aunyoneg. atdues
T g e 3 )sE[iglir
LS4 AR 3|E2
v nm Solp8 | 8 72 08)08
A e
&5 (55 zg|3% 23
s 7 i ZE]° s
PeSig=d o pamd BRI TS| T T T T T T | (9n0qE wol weseys )
g SR TR .
S R S0 RO S = =
ey e Bt o s sy
- 0 o T [as-Le-en
s o fdes 0 #voREnD #oloig 3 2u0ug
R — ShS ah  weTeTeRo = s
RS 25 g | CTNS TR MR
e R S P sy
ssapoy | s Auedwos
e B R
T 50 i wney m
o0gown um pRISURA 08E [ oD SoN 809 O B3N Py opew00D 9v) X
i0
<
AQOLSND 40 NIVHD Q





[image: image2.emf]
QA/QC Plan for Sampling from SHE-2, 26 Jan 2010 

Page 2 of 5
License Number 3BC-SHE0919 Type “B”

CAM-3, Shepherd Bay, NU


