[image: image3.jpg]




QA/QC Plan for Sampling from
Final Discharge Point of Bermed Fuel Storage Facilities at

CAM-M, CAM-3, FOX-M, FOX-3, DYE-M, and BAF-3
Licensee:
Department of National Defence,


Government of Canada

Licenses, Locations, & Monitoring Station #s:
	Licence
	Location
	Monitoring Station #
(Final Discharge Point of Bermed Fuel Storage Facility)

	3BC-CAM0919 Type “B”
	CAM-M North Warning System Site,

Cambridge Bay, Victoria Island, 

Kitikmeot Region, Nunavut
	CDL-3

	3BC-SHE0919 
Type “B”
	CAM-3 North Warning System Site,
Shepherd Bay, 

Kitikmeot Region, Nunavut
	SHE-3

	3BC-FOH0919 
Type “B”
	FOX-M North Warning System Site,
Hall Beach, Melville Peninsula, Qikiqtani Region, Nunavut
	FOH-3

	3BC-FOD0919 
Type “B”
	FOX-3 North Warning System Site,
Dewar Lakes, 

Qikiqtani Region, Nunavut
	FOD-3

	3BC-DYE0919 
Type “B”
	DYE-M North Warning System Site,

Cape Dyer, 

Qikiqtani Region, Nunavut
	DYE-3

	3BC-BAF0919 
Type “B”
	BAF-3 North Warning System Site,

Brevoort Island, 

Qikiqtani Region, Nunavut
	BAF-4


Plan submitted by:  Nasittuq Corporation
Date:

27 January 2010

Objective
This QA/QC plan applies to the six sites listed above at the monitoring stations for the final discharge point of each bermed fuel storage facility.  It has been prepared to ensure that sampling, sample preservation, and analyses are done in accordance with methods in the current edition of the Standard Methods for the Examination of Water and Wastewater as required by the Nunavut Water Board Water Licences listed above.
Review

This plan shall be reviewed annually by Nasittuq’s Environmental Services and will be updated as required.  Updated plans will be submitted to the NWB with an approval letter from a laboratory accredited to ISO/IEC Standard 17025.
Feedback
Feedback such as comments, complaints, and suggestions for improvements are to be submitted to:  Nasittuq Corp., 100-170 Laurier Ave. W., Ottawa, ON, K1P 5V5, Attention: Supervisor, Environmental Services.

Approval

This plan has been reviewed and accepted.

Original signed by Barb Thomson


27 Jan 2010
_________________________________

________________
Supervisor, Environmental Services


Date (dd/mm/yy)

Nasittuq Corp.
Background
Some fuel storage tanks at the six sites are surrounded by berms.  Water from precipitation accumulates in the berms and must be pumped out to prevent damage to the fuel tanks.
The water licenses require that prior to release of the effluent, samples must be taken and analyzed for the stated parameters.  If the results don’t exceed the effluent quality limits, then the water can be pumped out.  However, if the results do exceed the effluent quality limits, then the effluent is considered hazardous waste and must be disposed of off-site at an approved, licensed facility.
Samples are taken from each berm.  This sampling point is the final discharge point of the bermed fuel storage facility.  The liquid is adequately represented by single grab samples.
Equipment
The Berm Water Testing Kit is a cooler which contains:
- a Chain of Custody form which includes an area for the sample analysis request;

- cold packs; and 
- sample bottles (including bubble pack for glass bottles)
provided by Exova Accutest Laboratories.  The sample bottles are listed in Table 1 below.
The sample bottles are clean and free of contaminants.

Personal Protective Equipment (PPE)
Eye protection (safety glasses or goggles) and acid-resistant gloves are to be worn.  A filled portable eye wash or source of water to flush eyes must be on-hand at the sampling point.

Table 1.  Sample bottle requirements
	Bottle
	Parameters
	Sampling
	Storage Instructions

	250 ml plastic chem. bottle 
(no preservative)
	pH
	Grab
	Keep cool.  Return to the laboratory within 7 days of sampling.

	1 liter amber glass 
(no preservative)
	Oil & Grease (total)
	Grab
	Keep cool.  Return to the laboratory within 7 days of sampling.

	125 ml plastic with HNO3 preservative
	Metals (total)
	Unfiltered.  No rinsing.  Be careful of concentrated acid preservative.
	Keep cool.  Be sure “total” is written on the bottle label.

	125 ml plastic with HNO3 preservative
	Metals (dissolved)
	Field-filtered to 0.45 um.  No rinsing.  Be careful of concentrated acid preservative.
	Keep cool.  Be sure “dissolved” is written on the bottle label.

	125 ml plastic with HNO3 + K2CR2O7 preservative
	Mercury (total)
	Unfiltered.  Be careful of acid preservative.
	Keep cool.

	125 ml amber glass with H2SO4 preservative
	Phenols
	No rinsing.  Be careful of concentrated acid preservative.
	Keep cool.

	1 liter amber glass 
(no preservative)
	PCBs
	Grab
	Keep cool.  Return to the laboratory within 7 days of sampling.

	2 x 40 ml VOC vials
	BTE
	Fill slowly and completely – no air bubbles present.
	Keep cool.  Holding time is 14 days.


Sample Collection
1. Co-ordinate taking the samples with the air cargo flight schedule to minimize sample storage time.
2. The day before sampling, get the cold packs from the berm water testing kit and place in freezer overnight.
3. The day of sampling, gather these items at the sampling point:
a. eye protection (safety glasses or goggles);
b. acid- resistant gloves;
c.  filled portable eye wash or source of water to flush eyes;

d. Berm Water Testing Kit from Logistics;
e. 0.45 um filter units;
f. plastic bag (garbage bag is OK); and
g. permanent marker.
4. With permanent marker, mark each bottle with its parameter.  For the metals bottles, be sure to mark “Metals, total” or “Metals, dissolved”.  Mark each bottle with site, unique 
sample # (include tank ID), time, and date.
5. Put on PPE.  Have eye wash/water source within reach in case acid preservative splashes.
6. Fill and cap all bottles in kit as described in Table 1.
Note: Don't rinse the bottles before collecting the sample.
7. Wrap glass bottles with bubble pack from kit.

8. Pack bottles carefully in garbage bag and place in cooler.  Add cold packs.  Add cushioning material if required.
9. Complete Chain of Custody form.  See attached example.  Keep the pink sampler copy.  Place the remaining copies in the cooler.
10. Seal cooler with packing tape and air freight as soon as possible to: Exova Accutest Laboratories, 146 Colonnade Rd, Unit 8, Nepean, ON, Tel 613-727-5692.  

If any delay, keep samples cool (4 degrees C.).

Analyses
Exova Accutest Laboratories is accredited to ISO/IEC Standard 17025.  Exova has an established QA/QC program for the analyses required under this water licence.
Results

Results are sent to Nasittuq’s Supervisor, Environmental Services.

[image: image1.jpg]sy G - wOIRA KrEI00ET - o 5900

uo00m

TN T eted

T e e e e T P S sy T PO e S TS
oLt s i 59301 3 VO USG5 SIS U GO o S eSOV D1 s § S

v P
e
i "
- B D
F ol Al B W
va T R Rkl
2 T e L] Otovduns
ELEE L ==
SHEAR
1 HHE
F 4 HHE
PanRiged © i WP T| | T =] S[-[3[3Ta= T T N (anoge woy wasyp 5)
DECEEOEEm =
e o -
e R o ) —n i
——————— aameanieo 0 TR Cowee 5, Deeeeo
3 rRsp— SRS oA T T T S %
s N g o e s a1 NS 5K | G iy S s
e ISR sh-ow T o
= s

T 509 553 e e
"Lapu NO seuaed 18
09N P spomn 028 O

SR e 0
47 423 NO “umstuny
o) suon e O

AQOLSND 40 NIVHO

EZrT e ey

1AL323 NO 'wneio
o3 B spenoR0 s 3





[image: image2.emf]
QA/QC Plan for Sampling from Bermed Fuel Storage Facilities
Page 3 of  7
at CAM-M, CAM-3, FOX-M, FOX-3, DYE-M, & BAF-3

27 Jan 2010

