[image: image3.jpg]o Nunavut
Bltcunere Bisgd o 1002030400
NafgRa ilornete
ARCTIC ©Viord it A o
= GREENLAND
g Quarmag (Denmark)
A  GriséFiord
Pl
“Resolute BAFFIN BAY
; Noniivit
Koglaktok v«m?\m, ‘f‘“"'“
ol SRV | Wye s
# Pot Radum Rd Bl £ 'f'?(‘i
EIN S S e e U YT
A W;C'l it . o(Broughtonl)
Ko N -
P { :
bl ook~ N Pis il
Y o
NORTHWEST ; ) 4 R it e
TERRITORIES ChisiedmRaiE C. ) 8 COPEDORELS | "Rt~ OCEAN
i 5., it Coui
Gllawaiar e ok & v
z b3 3 5
ES o/ Gkl HUDSON
Westernr Churchill. AY 3
AL Gedtogat Prosince g iigiak
(S &
= FlinFlon The Sanikiluag
g i N‘ S Fonseem ® )
%
o SpMANTOn QuEBEC
& ! 3





OPERATING AND MAINTENANCE MANUAL
AGNICO-EAGLE MEADOWBANK PROJECT

BAKER LAKE FACILITIES

Prepared by:


Louise Grondin, P. Eng.









Vice-president Environment

Agnico-Eagle Mines Limited
Revision 0

October 19, 2007

Distribution List:

Nunavut Water Board

Baker Lake Hamlet

Roy Lindsay, Agnico-Eagle Baker Lake Office

Germain Cardinal, Agnico-Eagle Vancouver Office

Michael Hapqi, Agnico-Eagle Baker Lake Office

Nicolas Saucier, Agnico-Eagle, Baker Lake Office

Stéphane Robert, Agnico-Eagle, Technical Services

Larry Connell, Agnico-Eagle, Vancouver Office

Martin Bergeron, Agnico-Eagle, Vancouver Office

Daniel Kivari, Agnico-Eagle, Vancouver Office

Table of Contents
3Table of Contents


61.
INTRODUCTION


61.1
PURPOSE & SCOPE OF THE OPERATING AND MAINTENANCE MANUAL


61.2
CORPORATE STRUCTURE


71.3
ENVIRONMENTAL POLICY


82.
FACILITIES DESCRIPTION


113.
HAZARDOUS MATERIALS STORED ON SITE


134.
FACILITIES OPERATION AND MAINTENANCE


134.1.
SITE SECURITY


134.2.
PRODUCT IDENTIFICATION


144.3.
INVENTORY CONTROL


144.4.
WATER MANAGEMENT


144.5.
TESTING AND INSPECTION PROGRAM


154.6.
PREVENTIVE MAINTENANCE PROGRAM


164.7.
MATERIAL HANDLING AND TRANSFER


164.8.
SPILL CONTINGENCY PLAN





List of Tables

Table 1:
Consumable Chemical Materials that would transit through the Baker Lake Facilities

List of Figures

Figure 1:
Map of Nunavut showing the location of Baker Lake and of the Meadowbank Project

Figure 2:
AEM Initial Action Plan

Figure 3:
Spill Reporting Procedure

List of Appendices
APPENDIX A:
Meadowbank Baker Lake Facilities Drawings
APPENDIX B:
Meadowbank Gold Project – Water Use and Management Plan – Baker Lake Marshalling Area 
APPENDIX C:
Meadowbank Baker Lake Facilities Spill Contingency Plan 
1. INTRODUCTION

The Meadowbank Gold Project is located on Inuit-owned land in the Kivalliq Region of Nunavut, approximately 70 km north of Baker Lake (see Figure 1).  The gold will be extracted during the roughly eight- to ten-year operational lifespan of the mine.  All construction and operating supplies for the project will be transported on ocean freight systems to facilities constructed in the Hamlet of Baker Lake, which will include barge unloading facilities, laydown area, and fuel tank storage area.  The present Operating and Maintenance Manual is for the operation of these facilities.

1.1 PURPOSE & SCOPE OF THE OPERATING AND MAINTENANCE MANUAL
The purpose of the Meadowbank Baker Lake Facilities Operating and Maintenance Manual is to ensure that these facilities are operated, maintained and monitored in accordance with standardized preventive practices.  It also provides an all inclusive guide for the operators of the facilities and will be used to train personnel in the environmentally responsible operation of the facility.  

More specifically the objectives of this Operating and Maintenance Manual are to:

· ensure that a due diligence philosophy is used in the operation of the facilities;

· ensure that measures are in place in the event of a spill to prevent environmental contamination;

· ensure that water is managed with an objective to minimise any potential impacts on the aquatic ecosystem of the adjacent Baker Lake.
The present manual has been written in the spirit of an adaptive management philosophy and will be updated throughout the life of the facility to reflect operational experience and a continuous improvement objective.  
1.2 CORPORATE STRUCTURE
In early July 2007, Cumberland Resources became a 100% wholly-owned subsidiary of Agnico-Eagle Mines Limited (AEM).  Through a series of steps, AEM amalgamated with Cumberland and Meadowbank Mining Corporation (a wholly-owned subsidiary of Cumberland) on August 1, 2007.  As a result of this amalgamation, all of the rights, title, interests, liabilities and obligations of Cumberland and AEM are automatically, by law, transferred to and assumed by AEM.  Therefore in all the Water License documents, the terms ‘Cumberland’, ‘Meadowbank’, ‘AEM’ and ‘AEM’ are to mean the same entity: ‘Agnico-Eagle Mines Limited.

Agnico-Eagle Mines (AEM) Limited has its head office in Toronto at the following address:


Agnico-Eagle Mines Limited


145 King Street East, Suite 400


Toronto, Ontario, 


M5C 2Y7


Tel: 416-947-1212


Website: www.agnico-eagle.com
The Meadowbank project is managed out of the Vancouver office at the following address:


Agnico-Eagle Mines Limited


Suite 375, 555 Burrard Street, Box 209

Two Bentall Centre

Vancouver  British Columbia, V7X 1M8

Tel: 604-608-2557

The Baker Lake Facilities will be managed out of the Baker Lake office at the following address:


Agnico-Eagle Mines Limited


Baker Lake, Nunavut,


X0C 0A0


Tel: 867-793-4610
1.3 ENVIRONMENTAL POLICY
The present manual has been prepared in accordance with the commitments made in Agnico-Eagle’s environmental policy, which are to:

· Assess the potential environmental impacts of any new undertaking with an objective to minimise them.

· Design and operate our facilities to ensure that effective controls are in place to minimise risks to health, safety and the environment.

· Implement an emergency response plan to minimise the impacts of unforeseen events.

· Provide a professional environmental staff to plan and direct environmental compliance programs and to assist in training and education activities.

· Provide training and resources to develop environmentally responsible employees.

· Ensure that environmental factors are included in the purchase of equipment and materials.

· Ensure that contractors operate according to our environmental policy and procedures.

· Comply with all applicable environmental laws and regulations.

· Communicate with employees, the public, government agencies and other stakeholders on activities involving health, safety and the environment.

· Regularly verify environmental performance and implement any required corrective action.

· Minimise the generation of hazardous and non-hazardous waste and ensure proper disposal of all wastes.

· Implement measures to conserve natural resources such as energy and water.

· Rehabilitate sites in accordance with regulatory criteria and within the established time-frame.

2. FACILITIES DESCRIPTION
The proposed facilities at Baker Lake are located about 2 km east of the community and have the following coordinates (see Figure 1):
· Latitude: 64°19'2.42"N

Longitude: 96° 1'13.37"O

· UTM coordinates 644 025 E, 7 135 770 N

The facility will consist of a barge unloading ramp with an adjacent storage and marshalling area, a fuel storage facility, a storage compound for explosives (all explosives will be stored in approved magazines) and interconnecting roads. A total storage area of approximately 104,000 m2 will be provided by this facility, near the community of Baker Lake. The entire facility will be fenced and include an office trailer. Power for the facility will be supplied by portable generators and yard lighting will be provided by portable, diesel powered light towers. 

The Meadowbank Baker Lake facilities are shown in Appendix A.

Marshalling Area

The marshalling area will be used for interim storage of supplies for construction and operations of the Meadowbank Project.  The marshalling facility will receive supplies during the shipping season from late July until early October. The supplies will then be consolidated, sorted and transported to the site.  The site for the laydown area slopes up at about a 10% grade and is located at least 200 metres from the lake shore.  It will a terraced gravel based storage area for stacking sea containers and other equipment. The containers will be stacked two high. An appropriate container handler will be utilized to handle containers from the barge landing site and for transportation related loading.  A separate area will be lined with an HDPE liner for the storage of Ammonium Nitrate (AN).  This storage area will encompass approximately 6,600 m2, and will be located on the northwest side of the laydown area. The general laydown area will cover approximately 65,000 m2.

FIGURE 1

Map of Nunavut showing the location of Baker Lake and of the Meadowbank Project

[image: image2]

Tank Farm
The fuel tank farm will consist of four 10 ML diesel fuel storage tanks, two of which to be installed in 2007.  The fuel tank farm will be located adjacent to the marshalling area, approximately 300 metres from the shore of Baker Lake. These tanks will be field-erected steel tanks built to API-650 standards and located within a lined and bermed containment area, capable of containing 110% of the total volume of the tanks. 
The barges transporting diesel fuel to Baker Lake will be equipped with onboard transfer pumps to transfer fuel through a 200 mm hose connection to the storage tanks. A fuel pump module will be installed adjacent to the fuel storage tanks. The module will have high and low volumedispensing pumps to allow re-fuelling of highway vehicles, and the filling tanker trucks which will be used to haul fuel to site. The module will be housed in an arctic container installed on a lined and compacted gravel pad. The pump module will be provided with a spill collection sump and pumpout facilities.
The fuel storage facility will be contained within a lined and bermed area complete with the following:

· A granular base for the tank complete with a 60 mil HDPE liner system and granular dikes to suit the 2 - 10ML tanks

· Two 10ML tanks complete with the required appurtenances such as stairs, base manholes,water draw offs, re-supply nozzle, suction nozzle, tank lighting, tank level monitoring, roof manhole, manual gauge hatch, tank temperature and P/V Vent

· Piping for unloading and loading

· Site lighting via fixtures mounted from the dispensing building

· One Re-supply/Dispenser Building for loading the fuel Trailer / Truck and other vehicles. 
The fuel truck loading rates will be up to 50 m3/hr (15HP). Fuel loading rates will be up to 3 m3/hr (1.5HP) for small vehicles. This facility will be complete with temperature compensated metering system to manage fuel flows, safety valve to prevent loss of fuel from the fuel facility, fire extinguishers, building heating and ventilation systems, building lighting systems and controls systems for the pumps.
A fuel dispensing pad area complete with a dispensing unit will be in a lined facility with a provision to capture any and all spills at the fuelling area and direct it to the main containment area provided for the 2 - 10ML tanks. 

The facility is designed to meet the following standards:

· As a general guideline the fuel facility will meet the GN standard “Design Rationale for Fuel Storage & Distribution Facilities 1998”.

· National Fire Code 1995

· Proposed Federal Petroleum Products and Allied Petroleum Products Storage Tank System Regulations – 2003

·  Canadian Council of Ministers of the Environment “Environmental Code of Practice of Aboveground Storage Tank Systems Containing Petroleum Products – 1994”
At present, there are no plans to use water for hydrostatic testing of the integrity of the fuel tanks once they are erected. As with the 5 million litre tank that was previously permitted for the Meadowbank site, alternate testing methods will be used. These alternate methods of testing include: vacuum testing of the tank floor, shell to floor welds tested by penetrating oils, such as diesel and x-raying of welds to the extent required by API 650. These alternate testing methods have been successfully deployed at Diavik and Snap Lake Mines. Hydrostatic testing in cold weather is generally avoided because of potential icing after the testing is completed. 
Explosive Storage Compound
The explosives storage compound is located still farther up the slope, at a distance as required by explosive storage regulations. 
Roads

The roads will have an 8% gradient and will be covered with compacted granular fill.  

Drainage Control

Ditches will control run-off from roads and storage platform.  The contact run-off will be directed to an impervious sedimentation pond adjacent to the unloading platform.  Water management is covered in the Water Management Plan included in Appendix B.
3. HAZARDOUS MATERIALS STORED ON SITE
The tank farm will be used to store up to 40 million litres of diesel fuel for the construction, operation and all other activities at the Meadowbank project.

The marshalling area will be used as temporary storage for all the material that will be shipped by barges to Baker Lake for the construction and operation of the Meadowbank project.  The list of hazardous material that will transit through the marshalling area is the same as the list of hazardous material that will be used at the Meadowbank site and is reproduced in Table 3-1 from the Meadowbank License A application documents (Golder Report No. 457 – Hazardous Material Management Plan, August 24, 2007 and Golder Report No. 483 Spill Contingency Plan, August 27, 2007)

Table 1

Consumable Chemical Materials that would transit through the Baker Lake Facilities

	Large quantities required annually
	Relatively small quantities required annually

	Diesel, hydraulic, lube, oils and greases

Gasoline and Jet B aviation fuel

Ethylene glycol

Ammonium nitrate

Ammonium nitrate fuel oil (ANFO) explosive

Hydrated lime

Percol flocculent

Acetylene

Ferric sulphate or ferric chloride

Dynamite and packaged emulsion explosives

Emulsifiers (N7, N16, N23) for bulk emulsion explosives

Sodium nitrate

Glass beads for bulk emulsion explosives

Bulk emulsion boosters

Perimeter explosives

Paints

Solvents (varsol)

Batteries

Quicklime

Food products

High explosives detonators and blasting caps

Activated carbon (granular)

Anti-scalant

Sodium cyanide

Sodium hydroxide

Hydrochloric acid

Sulphur

Silica

Sodium metabisulphite

Copper sulphate

Borax

Shop supplies (batteries, hardware, fasteners, solvents, machining lubricants, etc.)

Surface and underground drilling consumables 
	Hydrofluoric acid

Nitric acid

Carbon dioxide*

Hydrogen peroxide or calcium peroxide*

Sulphuric acid*

Camp maintenance products (detergents, cleaning

fluids and powders, light bulbs, etc.)

Office supplies

Laboratory chemicals




4. FACILITIES OPERATION AND MAINTENANCE
The main components of the facilities operation, in place to ensure environmental protection, are as follows:

· Site security

· Product Identification

· Inventory Control

· Water Management 

· Testing and Inspection Program
· Preventive Maintenance Program

· Material Handling and Transfer

· Spill Contingency Plan

4.1. SITE SECURITY
Access to the site of the Tank Farm, the Explosive Storage facility and the Marshalling Area will be restricted to authorised personnel which have received the appropriate training.  The facilities will be fenced and a surveillance camera installed for monitoring.  

Signs will be posted to indicate that access is restricted.
4.2. PRODUCT IDENTIFICATION
All containers stored at the Marshalling area should be identified with the product information found on the Material Safety Data Sheets.
The fuel tank at the tank farm should be identified with the product they contain, the tank capacity and the year of construction.
All products stored at the Explosive Storage Facility should have proper identification and signs should be posted as specified in the regulations.

4.3. INVENTORY CONTROL
An inventory control system will be in place at the Tank Farm, the Explosive Storage Facility and at the Marshalling area to ensure that all material and fuel is accounted for.  This system will include inventory reconciliation with a provision for reporting to management of discrepancies in inventories.  
4.4. WATER MANAGEMENT
A water use and management plan was prepared for the facility and it is included in Appendix B.
4.5. TESTING AND INSPECTION PROGRAM
Tank Farm

The fuel storage tank system will be tested prior to the tank being placed in service and whenever a leak is suspected in the primary or secondary containment of the storage tanks, piping, containment sumps or related components.  Inventory control will also be used as a leak detection tool.

The following inspections of the fuel tank systems will be carried out:

· Routine daily visual inspection of the storage tank facility to ensure that there has not been a leak or deterioration of the facility that could result in a leak, will be conducted and documented in a log book.

· Routine weekly inspection of the storage tank facility will be conducted and documented in an inspection form.  These inspections will look at:

(a) foundations, tank walls, roof, and tank attachments;

(b) dyke capacity, condition of the dyke wall and floor, and water removal systems;

(c) pumps and product-handling equipment;

(d) tank gauging equipment;

(e) mechanical and automatic electronic leak detection equipment;

(f) dispenser sumps and spill containment devices; and

(g) overfill protection devices.

· Annual inspection and performance testing will be conducted on the storage tank facility and documented by an external authorised inspector.
Any deficiencies in a storage tank system identified as a result of the above inspections specified will be documented and reported to management who will promptly correct it. 

Marshalling Area
The storage containers should be inspected for damage upon reception and prior to storage.  Any damaged container that could lead to a contaminant spill should be set aside and provide with secondary containment or repaired if possible.  The storage will be organised to prevent storage of incompatible products side by side.

In addition to inventory control inspection, the following inspections of the marshalling area will be carried out:

· Routine daily visual inspection of the storage area to ensure that the containers storage is physically stable, the inspection will be recorded in a log book;

· Monthly inspection of the storage facility will be conducted and documented in an inspection form.  These inspections will look at:

(a) marshalling area foundations, roof, and walls;

(b) sump capacity, condition of the dyke wall and floor, and water removal systems;

(c) product-handling equipment;

(d) signs of spilled material; and

(d) spill containment devices (ex: is the spill kit complete)
Any deficiencies in a storage tank system identified as a result of the above inspections specified will be documented and reported to management who will promptly correct it. 

Explosive Storage Area
The storage containers should be inspected for damage upon reception and prior to storage.  Any damaged container will be supplied with secondary containment or repaired.

In addition to inventory control inspections, the following inspections will take place:
· Routine daily visual inspection of the storage area to ensure that the explosive storage is physically stable, and done according to standard practices, the inspection will be recorded in a log book.
· Monthly inspection of the storage facility will be conducted and documented in an inspection form.  These inspections will look at:

(a) building or container foundations, roof, and walls (for deterioration);

(b) signs of spilled material; and

(c) spill containment devices (ex: is the spill kit complete)
Any deficiencies in a storage tank system identified as a result of the above inspections specified will be documented and reported to management who will promptly correct it. 

4.6. PREVENTIVE MAINTENANCE PROGRAM
In addition to maintenance resulting from inspection, the main components of the facilities will be placed on a preventive maintenance program which will ensure that components will be inspected and replaced before failure.  The program will be managed with the J.D. Edwards maintenance program in use at all Agnico-Eagle facilities.
4.7. MATERIAL HANDLING AND TRANSFER
Fuel Tank

The personnel responsible for transferring fuel will have received training to ensure that all reasonable steps will be taken to prevent spills, such as:

 (1) When a tank vehicle is being unloaded, the vehicle operator shall remain:

(a) in constant view of the fill pipe; and

(b) in constant attendance at the delivery control valve. (See Appendix B, note

(2) Standard procedures for normal operation, as well as for emergencies, shall be posted in printed form for convenient reference. 
Marshalling Area

The personnel responsible for unloading barges into the marshalling area and for loading trucks for transportation to the Meadowbank project will have received training to ensure that all reasonable steps will be taken to prevent spills, such as:

(1) Ensure that the lifting capacity of the lifting device matches the load to be carried;

(2) Ensure that the containers are transported to the specified areas of the marshalling area (incompatible materials should not be placed side-by-side);

(3) Ensure that container stacking leads to a physically stable storage.
(4) Emergency and spill procedures will be posted in printed form for convenient reference. 
The Material Safety Data Sheets of the stored products should be kept in the storage area

Explosive Storage Area

The personnel responsible for transferring explosive material will need to be certified and as part of their training they will receive instructions to ensure that all reasonable steps will be taken to prevent spills.  Training will be done according to the applicable explosives regulations (Explosives Regulations, R.R.N.W.T. 1990 c. E-27).  Emergency and spill procedures will be posted in printed form for convenient reference.  
The Material Safety Data Sheets of the stored products should be kept in the storage area.

4.8. SPILL CONTINGENCY PLAN
A spill contingency plan has been prepared for the Baker Lake Facilities and is included in Appendix C.  For the purposes of this plan, a spill is defined as an accidental release of product into the environment that has the potential for adverse impact. 
The plan is summarised in Figure 2 and 3.

Figure 2: AEM Action Plan in the Event of a Spill

[image: image1.jpg]AEM




ENSURE SAFETY 


ENSURE SAFETY OF YOURSELF & OTHERS






The First Responder will:

• call the On-Site Coordinator for assistance

• secure the area to ensure personnel and site safety

• assess hazards and attend to injured


IDENTIFY & CONTAIN 
IDENTIFY & CONTAIN THE SPILL USING SPILL RESPONSE ACTION INFORMATION


The First Responder will identify the type of spill and category and IF SAFE TO DO SO contain the spill.


REPORT
REPORT TO THE ON SCENE COORDINATOR

The First Responder will report the spill to the On-Site Coordinator, including the spill type, location, cause, and volume .

NOTIFY
NOTIFICATION:


The On-Site Coordinator will:

• notify the Mine General Manager immediately.
If the estimated spilled quantity > quantity in Table 2 or if the spill has entered a watercourse: 

The Mine General Manager will:

• contact the Environmental Advisor (Regional Manager of Environment,  Social and Government Affairs) immediately who will report the 24-HR Report line:867-920-8130 first, then INAC and EC, and

• Notify the Regional General Manager within 24 hours 

ALERT




ALERT THE EMERGENCY RESPONSE TEAM (ERT)

The On-Site Coordinator will contact the ERT and be a liaison between all parties


RECORD



RECORD THE FACTS OF THE SPILL

The On-Site Coordinator will ensure that the following 

forms are complete:

· spill report forms (see attached)

· incident report forms 

· photographs


INVESTIGATE
If an investigation is requested by the Environmental Advisor or the Safety Coordinator, within 2 days of the spill, the Mine General Manager will appoint the investigation team comprising:
· a senior level manager as tem leader
· members with relevant expertise

· at least one member independent of the operation

· representatives from the environmental and safety department


RECOMMEND
Within 20 days, the Investigation Team leader sends the conclusions to the Mine General Manager
Figure 3

Spill Reporting Procedure

FIRST RESPONDER

ON-SCENE COORDINATOR

name (primary)
Roy Lindsay
name (alternate)
Germain Cardinal


Phone: number: 
day: : 867-793-4610


night: 867.793.4302

MINE GENERAL MANAGER
Assists and notifies as required





ENV. ADVISOR
Regional Manager 


ERT

Environment, Social &

EMERGENCY
Gov. Affairs


RESPONSE TEAM

Contacted



Activated





24-HOUR
SPILL REPORT LINE




867 920 8130










Notified if required





REGIONAL GENERAL
MANAGER

Contacted within 24 hours

Provides resources

Meadowbank Baker Lake Facilities – Operating and Maintenance Manual 

October 2007, revision 0

